## Instructions
Light Pollution and Energy Efficiency Cost Calculation Tool
This spreadsheet is used to calculate the payback period and return on investment (ROI) for the lighting application scenarios in the "Choosing Both Energy Efficiency and Light Pollution Mitigation for Commercial Outdoor Lighting" study.
Instructions
| 1) | Provide the most accurate estimates possible for the editable fields in this spreadsheet. Sheets containing editable fields have their sheet tabs highlighted with a light yellow/peach color (see key below). This is the same color as the editable fields. Editable fields include fixture quantities, fixture costs, fixture installation costs, cost markups, maintenance costs (material, labor, and markup), factors impacting rebates, and more. Important colors for cells are shown below:
Fields that contain estimated quantities that impact the payback period and ROI. Intended to be edited.
Fields that contain formulae or fixed reference values. Do not edit.
Table headers and reference information.
| 2) | After accurate estimates have been provided, go to the "Dashboard" tab and modify the master parameters. These include system lifetime, electricity costs, control schedule (i.e., dimming schedule), and LED fixture failure rate parameters.
| 3) | Results (payback period and ROI) on the "Dashboard" tab will automatically update.
Sheet Descriptions
Tab Color Legend:
This color is reserved for the main dashboard.
Sheet tabs with this color contain editable fields that are likely to impact payback and ROI calculations.
Sheet tabs with this color contain summary information in tabular form, graphical form, or both.
Dashboard
This sheet serves as the main user interface. Use this sheet to modify global parameters and instantly update the estimate payback periods and ROI. Editable parameters include system lifetime (which impacts the frequency of lamp, ballast, and fixture replacements), electricity costs (split into summer, winter, and monthly service charge), a lighting power schedule for dimming calculations, and parameters for LED catastrophic fixture and ballast failure rates.
Base_Energy
This sheet is formatted as a fixture schedule for the base case lighting application scenarios and is primarily used to estimate the total power consumption of the base case application scenarios. Editable fields include the number (quantity) of each fixture type and their associated per-unit power consumption.
Capital_R1
This sheet is formatted as a fixture schedule for the lighting application scenarios in Retrofit Scenario 1. This sheet is used to calculate the capital cost of these lighting systems; the power consumption values on this sheet feed the "Energy" sheet for calculation of the total power consumption of the lighting scenario.
Capital_R2
This sheet is formatted as a fixture schedule for the lighting application scenarios in Retrofit Scenario 2. This sheet is used to calculate the capital cost of these lighting systems; the power consumption values on this sheet feed the "Energy" sheet for calculation of the total power consumption of the lighting scenario.
Capital_Summary (Ref)
This sheet provides tabular and graphical summary information for the Capital Costs for all lighting application scenarios. Values on this sheet are automatically calculated from the capital cost sheets and should not be edited directly.
Maint_Base
This sheet is formatted as a fixture schedule for the Base Case lighting application scenarios. This sheet is used to calculate the maintenance cost of these lighting systems. Fixture quantities in this sheet are not automatically fed from other sheets (e.g., the capital cost sheets) to allow maintenance cost estimations for a different quantity of fixtures.
Maint_R1
This sheet is formatted as a fixture schedule for the lighting application scenarios In Retrofit Scenario 1. This sheet is used to calculate the maintenance cost of these lighting systems. Fixture quantities in this sheet are not automatically fed from other sheets (e.g., the capital cost sheets) to allow maintenance cost estimations for a different quantity of fixtures.
Maint_R2
This sheet includes acceptable alternative version of the Color Vector Graphic. It also stores data used to generate the graphics.
Maint_Summary (Ref)
This sheet provides tabular and graphical summary information for the Maintenance Costs for all lighting application scenarios. Values on this sheet are automatically calculated from the capital cost sheets and should not be edited directly.
Energy
This sheet is used to calculate quantities associated with power and energy consumption (including annual energy cost and annual energy cost savings). All quantities in this sheet are computed automatically and should not be edited directly.
Rebates
This sheet is used to calculate rebates provided by two rebate providers local to Colorado, Xcel Energy and Fort Collins Utility. This sheet contains editable fields for estimating the rebates.
ROI (Ref)
This sheet is used to calculate the payback periods and ROI. All quantities in this sheet are computed automatically and should not be edited directly.
OpHrs (Ref)
This sheet is used to calculate the operating hours---between various time points of interest---for each day of the year. This sheet feeds the "OpHrs_Summary (Ref)" where hour totals are calculated.
OpHrs_Summary (Ref)
This sheet provides a tabular summary of the annual operating hours.
Contributors
Valeria Holland, VH Lighting Services LLC
Tony Esposito, Lighting Research Solutions LLC

## Dashboard
DASHBOARD
| MASTER INPUTS | [6 empty] | RESULTS
| Lifetime Period | 20 | years | [5 empty] | Payback
[8 empty] | Scenario | (Years) | ROI
Model High School - Base Case
| Electricity Cost | [6 empty] | Model High School - Retrofit 1 (50% dim) | 5.6827 | 17.6%
[8 empty] | Model High School - Retrofit 2 (80% dim) | 5.0744 | 19.71%
| Summer | 0.1071 | /kWh |  |  |  |  | College Ave (Roadway) - Base Case
| Winter | 0.1208 | /kWh |  |  |  |  | College Ave (Roadway) - Retrofit 1 (50% dim) | 12.8617 | 7.775%
| Service Charge | 0 | /Month |  |  |  |  | College Ave (Roadway) - Retrofit 2 (80% dim) | 13.6616 | 7.32%
College Ave (Area) - Base Case
| Rebate Provider | 2 | 1 = Xcel |  |  |  |  | College Ave (Area) - Retrofit 1 (50% dim) | 3.848 | 25.99%
|  |  | 2 = Fort Collins Utility |  |  |  |  | College Ave (Area) - Retrofit 2 (80% dim) | 3.9425 | 25.36%
College Ave (Decorative) - Base Case
[8 empty] | College Ave (Decorative) - Retrofit 1 (50% dim) | 10.2864 | 9.722%
| Lighting power and dimming schedule | [6 empty] | College Ave (Decorative) - Retrofit 2 (80% dim) | 13.5956 | 7.355%
|  | Model High School |  |  | College Ave
|  | Base | R1 | R2 | Base | R1 | R2
| Dusk - Midnight | 100% | 100% | 100% | 100% | 100% | 100%
| Midnight - 3 am | 100% | 50% | 20% | 100% | 100% | 100%
| 3 am - Dawn | 100% | 50% | 20% | 100% | 50% | 20%
LED Lifetime Failure Rates
| Fixtures | 1% | [LINK] | [LINK2]
| Driver | 0.2% | [LINK]
Note on C11: June - September
Note on C12: January - May October - December
Note on C29: The percentage of LED failures that require a full replacement of the LED head. These failure incur the full capital cost of the fixture (material) and labor costs for installation.
Note on C30: The percentage of drivers per 1000 hours of operation that fail. These failures iincur material cost for the driver replacement and labor cost for installation.

## Base_Energy
Energy Consumption - Base Case
Model High School
Power Consumption [W]
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty
A | Holophane | SMST400MH00XXPM | 18 |  | 442 | 7956
B | Holophane | SMST400MH00XXPM | 4 |  | 442 | 1768
B2@180 | Holophane | SMST400MH00XXPM | 10 | 2 fixtures at 180 degrees | 884 | 8840
P | Holophane | W435MH00UX | 16 |  | 126 | 2016
W1 | Holophane | SMST70MH00XXPM | 19 |  | 183 | 3477
W2 | Holophane | W4150MH00UX | 1 |  | 88 | 88
C | Bega | 7275MH | 6 |  | 44 | 264
`
[5 empty] | Total | 24409
College Ave (Roadway)
Power Consumption [W]
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty
C2@180 R1 | Lithonia | ATRL G XXXXX R3 | 3 | 2 fixtures at 180 degrees | 920 | 2760
Controls | Acuity |  | 1
[5 empty] | Total | 2760
College Ave (Area)
Power Consumption [W]
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty
AR1 | Lithonia | RSX4 LED P2 40K R3 | 5 |  | 1080 | 5400
Controls | Acuity |  | 1
[5 empty] | Total | 5400
College Ave (Decorative)
Power Consumption [W]
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty
B2@180 TWIN R1 | Holophane | AWDE3 P70 40K XXX AL5 | 10 | 2 fixtures at 180 degrees - twin | 566 | 5660
Controls | Acuity |  | 1
[5 empty] | Total | 5660

## Capital_R1
Capital Cost - Retrofit Scenario 1 (RS1)
Model High School
[5 empty] | Power Consumption [W] |  |  | +ED Markup | +EC Markup | +Tax |  |  | +Labor markup
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty | DN Pricing (unit) | 15% | 20% | 7.55% | QTY Material Cost | Labor cost | 0% | QTY Labor Cost | UNIT Total Cost | QTY Total Cost
AR1 | Lithonia | RSX2 LED P6 40K R3 | 18 |  | 247 | 4446 | 651.42 | 749.133 | 898.9596 | 966.831 | 17402.9589 | 115 | 115 | 2070 | 1081.831 | 19472.9589
BR1 | Lithonia | RSX2 LED P6 40K R3 | 4 |  | 247 | 988 | 651.42 | 749.133 | 898.9596 | 966.831 | 3867.3242 | 172 | 172 | 688 | 1138.831 | 4555.3242
B2@180 R1 | Lithonia | RSX2 LED P6 40K R3 | 10 | 2 fixtures at 180 degrees | 494 | 4940 | 1302.844 | 1498.2706 | 1797.9247 | 1933.668 | 19336.6804 | 344 | 344 | 3440 | 2277.668 | 22776.6804
PR1 | Lithonia | DSX0 LED P1 40K 70CRI T2M | 16 |  | 33 | 528 | 703.12 | 808.588 | 970.3056 | 1043.5637 | 16697.0188 | 90 | 90 | 1440 | 1133.5637 | 18137.0188
W1R1 | Cree | C-WP-C-TR-S10L-SCCT-UL-DB | 19 |  | 68 | 1292 | 163 | 187.45 | 224.94 | 241.923 | 4596.5364 | 90 | 90 | 1710 | 331.923 | 6306.5364
W2R1 | Cree | C-WP-C-TR-S6L-SCCT-UL-DB | 1 |  | 16 | 16 | 135 | 155.25 | 186.3 | 200.3656 | 200.3656 | 90 | 90 | 90 | 290.3657 | 290.3657
CR1 | RAB | BLEDR24N | 6 |  | 23 | 138 | 832 | 956.8 | 1148.16 | 1234.8461 | 7409.0765 | 202.5 | 202.5 | 1215 | 1437.3461 | 8624.0765
Controls | Acuity |  | 1 |  |  |  | 13635 | 15680.25 | 18816.3 | 20236.9306 | 20236.9306 | 460 | 460 | 460 | 20696.9306 | 20696.9306
`
[5 empty] | Total | 12348 |  |  |  | Totals: | 89746.8914 |  |  | 11113 |  | 100859.8914
College Ave (Roadway)
[5 empty] | Power Consumption [W] |  |  | +ED Markup | +EC Markup | +Tax |  |  | +Labor markup
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty | DN Pricing (unit) | 15% | 20% | 7.55% | Material Cost | Labor cost | 0% | QTY Labor Cost | UNIT Total Cost | Total Cost
C2@180 R1 | Lithonia | ATRL G XXXXX R3 | 3 | 2 fixtures at 180 degrees | 558 | 1674 | 1312 | 1508.8 | 1810.56 | 1947.2573 | 5841.7718 | 230 | 230 | 690 | 2177.2573 | 6531.7718
Controls | Acuity |  | 1 |  |  |  | 4454.41 | 5122.5715 | 6147.0858 | 6611.1908 | 6611.1908 | 460 | 460 | 460 | 7071.1908 | 7071.1908
[5 empty] | Total | 1674 |  |  |  | Totals: | 12452.9626 |  |  | 1150 |  | 13602.9626
College Ave (Area)
[5 empty] | Power Consumption [W] |  |  | +ED Markup | +EC Markup | +Tax |  |  | +Labor markup
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty | DN Pricing (unit) | 15% | 20% | 7.55% | Material Cost | Labor cost | 0% | QTY Labor Cost | UNIT Total Cost | Total Cost
AR1 | Lithonia | RSX4 LED P2 40K R3 | 5 |  | 320 | 1600 | 1141.7 | 1312.955 | 1575.546 | 1694.4997 | 8472.4986 | 259.5 | 259.5 | 1297.5 | 1337.6733 | 9769.9986
Controls | Acuity |  | 1 |  |  |  | 4135.57 | 4755.9055 | 5707.0866 | 6137.9716 | 6137.9716 | 460 | 460 | 460 | 20826.3754 | 6597.9716
[5 empty] | Total | 1600 |  |  |  | Totals: | 14610.4703 |  |  | 1757.5 |  | 16367.9703
College Ave (Decorative)
[5 empty] | Power Consumption [W] |  |  | +ED Markup | +EC Markup | +Tax |  |  | +Labor markup
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty | DN Pricing (unit) | 15% | 20% | 7.55% | Material Cost | Labor cost | 0% | QTY Labor Cost | UNIT Total Cost | Total Cost
B2@180 TWIN R1 | Holophane | AWDE3 P70 40K XXX AL5 | 10 | 2 fixtures at 180 degrees - twin | 312 | 3120 | 1736 | 1996.4 | 2395.68 | 2576.5538 | 25765.5384 | 230 | 230 | 2300 | 2806.5538 | 28065.5384
Controls | Acuity |  | 1 |  |  |  | 4706.17 | 5412.0955 | 6494.5146 | 6984.8505 | 6984.8505 | 460 | 460 | 460 | 7444.8505 | 7444.8505
[5 empty] | Total | 3120 |  |  |  | Totals: | 32750.3889 |  |  | 2760 |  | 35510.3889
Note on H5: DN = Distributor Net DN price represents the incurred cost to consumers.
Note on H13: Note: Cost of sensors, wall switch, relays, repeater plus "the brain" of the system and commissioning
Note on H20: DN = Distributor Net DN price represents the incurred cost to consumers.
Note on H22: Note: Cost of sensors, wall switch, repeater plus "the brain" of the system and commissioning
Note on H29: DN = Distributor Net DN price represents the incurred cost to consumers.
Note on H38: DN = Distributor Net DN price represents the incurred cost to consumers.
Note on I4: ED = Electrical Distributor This column is used to account for the markup applied by the electrical distributor.
Note on I19: ED = Electrical Distributor This column is used to account for the markup applied by the electrical distributor.
Note on I28: ED = Electrical Distributor This column is used to account for the markup applied by the electrical distributor.
Note on I37: ED = Electrical Distributor This column is used to account for the markup applied by the electrical distributor.
Note on J4: ED = Electrical Contractor This column is used to account for the markup applied by the electrical contractor.
Note on J19: ED = Electrical Contractor This column is used to account for the markup applied by the electrical contractor.
Note on J28: ED = Electrical Contractor This column is used to account for the markup applied by the electrical contractor.
Note on J37: ED = Electrical Contractor This column is used to account for the markup applied by the electrical contractor.
Note on M5: Labor costs taken from FSG
Note on M13: Labor cost for control system equal to 4 hours at $115 per hour. Values provided by Facility Solutions Group (FSG).
Note on M20: Labor costs taken from FSG
Note on M22: Labor cost for control system equal to 4 hours at $115 per hour. Values provided by Facility Solutions Group (FSG).
Note on M29: Labor costs taken from FSG
Note on M30: Valeria Holland: Labor cost + truck rental cost
Note on M31: Labor cost for control system equal to 4 hours at $115 per hour. Values provided by Facility Solutions Group (FSG).
Note on M38: Labor costs taken from FSG
Note on M40: Labor cost for control system equal to 4 hours at $115 per hour. Values provided by Facility Solutions Group (FSG).
Note on N4: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on N19: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on N28: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on N37: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.

## Capital_R2
Capital Cost - Retrofit Scenario 2 (RS2)
Model High School
[5 empty] | Power Consumption [W] |  |  | +ED Markup | +EC Markup | +Tax |  |  | +Labor markup
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty | DN Pricing (unit) | 15% | 20% | 7.55% | QTY Material Cost | Labor cost | 0% | QTY Labor Cost | UNIT Total Cost | QTY Total Cost
AR2 | Lithonia | RSX2 LED P6 30K R3 | 13 |  | 247 | 3211 | 651.42 | 749.133 | 898.9596 | 966.831 | 12568.8036 | 115 | 115 | 1495 | 1081.831 | 14063.8036
AR2@180 | Lithonia | RSX2 LED P2 30K R3 | 2 | 2 fixtures at 180 degrees | 228 | 456 | 1162.72 | 1337.128 | 1604.5536 | 1725.6974 | 3451.3948 | 344 | 344 | 688 | 2069.6974 | 4139.3948
AR2@180_B | Lithonia | RSX2 LED P2 30K R3S | 1 | 2 fixtures at 180 degrees | 228 | 228 | 1162.72 | 1337.128 | 1604.5536 | 1725.6974 | 1725.6974 | 344 | 344 | 344 | 2069.6974 | 2069.6974
AR2_B | Lithonia | RSX2 LED P2 30K R3 | 5 |  | 114 | 570 | 581.36 | 668.564 | 802.2768 | 862.8487 | 4314.2435 | 115 | 115 | 575 | 977.8487 | 4889.2435
AR2_HS | Lithonia | RSX2 LED P2 30K R2 HS | 3 |  | 114 | 342 | 615 | 707.25 | 848.7 | 912.7768 | 2738.3306 | 172 | 172 | 516 | 1084.7768 | 3254.3306
B2@180 R2_B | Lithonia | RSX2 LED P4 30K R3 | 7 | 2 fixtures at 180 degrees | 380 | 2660 | 1204.78 | 1385.497 | 1662.5964 | 1788.1224 | 12516.857 | 344 | 344 | 2408 | 2132.1224 | 14924.857
BR2_B | Lithonia | RSX2 LED P4 30K R3 | 1 |  | 190 | 190 | 602.39 | 692.7485 | 831.2982 | 894.0612 | 894.0612 | 172 | 172 | 172 | 1066.0612 | 1066.0612
PR2 | Lithonia | DSX0 LED P1 30K 70CRI T2M | 16 |  | 33 | 528 | 703.12 | 808.588 | 970.3056 | 1043.5637 | 16697.0188 | 90 | 90 | 1440 | 1133.5637 | 18137.0188
W1R2 | Cree | XSPW-B-WM-4ME-8L-30K-UL | 19 |  | 77 | 1463 | 344.7 | 396.405 | 475.686 | 511.6003 | 9720.4056 | 90 | 90 | 1710 | 601.6003 | 11430.4056
W2R2 | Cree | XSPW-B-WM-4ME-2L-30K-UL | 1 |  | 20 | 20 | 344.7 | 396.405 | 475.686 | 511.6003 | 511.6003 | 90 | 90 | 90 | 601.6003 | 601.6003
CR2 | Signify | PBL-14L-450-WW-G2-5-UNV | 6 |  | 23 | 138 | 742 | 853.3 | 1023.96 | 1101.269 | 6607.6139 | 202.5 | 202.5 | 1215 | 1303.769 | 7822.6139
Controls | Acuity |  | 1 |  |  |  | 13635 | 15680.25 | 18816.3 | 20236.9306 | 20236.9306 | 460 | 460 | 460 | 20696.9306 | 20696.9306
[5 empty] | Total | 9806 |  |  |  | Total | 91982.9572 |  |  | 11113 |  | 103095.9572
College Ave (Roadway)
[5 empty] | Power Consumption [W] |  |  | +ED Markup | +EC Markup | +Tax |  |  | +Labor markup
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty | DN Pricing (unit) | 15% | 20% | 7.55% | QTY Material Cost | Labor cost | 0% | QTY Labor Cost | UNIT Total Cost | QTY Total Cost
C2@180 R2B | Cree | RSWX-B-HT-3ME-32L-30K7-Ux-xx-N | 3 | 2 fixtures at 180 degrees | 496 | 1488 | 1950 | 2242.5 | 2691 | 2894.1705 | 8682.5115 | 230 | 230 | 690 | 3124.1705 | 9372.5115
Controls | Acuity |  | 1 |  |  |  | 4454.41 | 5122.5715 | 6147.0858 | 6611.1908 | 6611.1908 | 460 | 460 | 460 | 7071.1908 | 7071.1908
[5 empty] | Total | 1488 |  |  |  | Total | 15293.7023 |  |  | 1150 |  | 16443.7023
College Ave (Area)
[5 empty] | Power Consumption [W] |  |  | +ED Markup | +EC Markup | +Tax |  |  | +Labor markup
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty | DN Pricing (unit) | 15% | 20% | 7.55% | QTY Material Cost | Labor cost | 0% | QTY Labor Cost | UNIT Total Cost | QTY Total Cost
AR2 | Lithonia | RSX4 LED P3 30K R3 | 5 |  | 369 | 1845 | 1141.7 | 1312.955 | 1575.546 | 1694.4997 | 8472.4986 | 259.5 | 259.5 | 1297.5 | 1953.9997 | 9769.9986
Controls | Acuity |  | 1 |  |  |  | 4135.57 | 4755.9055 | 5707.0866 | 6137.9716 | 6137.9716 | 460 | 460 | 460 | 6597.9716 | 6597.9716
[5 empty] | Total | 1845 |  |  |  | Total | 14610.4703 |  |  | 1757.5 |  | 16367.9703
College Ave (Decorative)
[5 empty] | Power Consumption [W] |  |  | +ED Markup | +EC Markup | +Tax |  |  | +Labor markup
Type | Manufacturer | Catalog Number | Quantity | Notes | Unit | Qty | DN Pricing (unit) | 15% | 20% | 7.55% | QTY Material Cost | Labor cost | 0% | QTY Labor Cost | UNIT Total Cost | QTY Total Cost
B2@180 TWIN R2 | Signify | RN30-145W64LED3K-G3-LE5F | 10 | 2 fixtures at 180 degrees - twin | 280 | 2800 | 2655 | 3053.25 | 3663.9 | 3940.5244 | 39405.2445 | 230 | 230 | 2300 | 4170.5244 | 41705.2445
Controls | Acuity |  | 1 |  |  |  | 4706.17 | 5412.0955 | 6494.5146 | 6984.8505 | 6984.8505 | 460 | 460 | 460 | 7444.8505 | 7444.8505
[5 empty] | Total | 2800 |  |  |  | Total | 46390.095 |  |  | 2760 |  | 49150.095
Note on H5: DN = Distributor Net DN price represents the incurred cost to consumers.
Note on H17: Valeria Holland: Note: Cost of sensors, wall switch, relays, repeater plus "the brain" of the system and commissioning
Note on H24: DN = Distributor Net DN price represents the incurred cost to consumers.
Note on H26: Note: Cost of sensors, wall switch, repeater plus "the brain" of the system and commissioning
Note on H33: DN = Distributor Net DN price represents the incurred cost to consumers.
Note on H42: DN = Distributor Net DN price represents the incurred cost to consumers.
Note on I4: ED = Electrical Distributor This column is used to account for the markup applied by the electrical distributor.
Note on I23: ED = Electrical Distributor This column is used to account for the markup applied by the electrical distributor.
Note on I32: ED = Electrical Distributor This column is used to account for the markup applied by the electrical distributor.
Note on I41: ED = Electrical Distributor This column is used to account for the markup applied by the electrical distributor.
Note on J4: ED = Electrical Contractor This column is used to account for the markup applied by the electrical contractor.
Note on J23: ED = Electrical Contractor This column is used to account for the markup applied by the electrical contractor.
Note on J32: ED = Electrical Contractor This column is used to account for the markup applied by the electrical contractor.
Note on J41: ED = Electrical Contractor This column is used to account for the markup applied by the electrical contractor.
Note on M5: Labor costs taken from FSG
Note on M17: Labor cost for control system equal to 4 hours at $115 per hour. Values provided by Facility Solutions Group (FSG).
Note on M24: Labor costs taken from FSG
Note on M26: Labor cost for control system equal to 4 hours at $115 per hour. Values provided by Facility Solutions Group (FSG).
Note on M33: Labor costs taken from FSG
Note on M34: Valeria Holland: Labor cost + truck rental cost
Note on M35: Labor cost for control system equal to 4 hours at $115 per hour. Values provided by Facility Solutions Group (FSG).
Note on M42: Labor costs taken from FSG
Note on M44: Labor cost for control system equal to 4 hours at $115 per hour. Values provided by Facility Solutions Group (FSG).
Note on N4: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on N23: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on N32: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on N41: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.

## Capital_Summary (Ref)
Capital Cost - SUMMARY
|  | Retrofit 1 |  |  | Retrofit 2
| Site | Material | Installation | Total | Material | Installation | Total
| Model High School | 89746.8914 | 11113 | 100859.8914 | 91982.9572 | 11113 | 103095.9572
| College Ave (Roadway) | 12452.9626 | 1150 | 13602.9626 | 15293.7023 | 1150 | 16443.7023
| College Ave (Area) | 14610.4703 | 1757.5 | 16367.9703 | 14610.4703 | 1757.5 | 16367.9703
| College Ave (Decorative) | 32750.3889 | 2760 | 35510.3889 | 46390.095 | 2760 | 49150.095

## Maint_Base
ANNUAL Maintenance Cost - Base Case
Model High School
[7 empty] | Relamping |  |  | 0% |  |  | Replace Ballast |  |  | 0% |  |  | Fixture Cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
A | Holophane | SMST400MH00XXPM | 18 |  | 10000 | 4304.6642 | 0.43047 | 38 | 115 | 115 | 65.8614 | 1185.5045 | 0.086093 | 55 | 57.5 | 57.5 | 9.6855 | 174.3389 | 0 | 57.5 | 57.5 | 0 | 0 | 75.5469 | 1359.8434
B | Holophane | SMST400MH00XXPM | 4 |  | 10000 | 4304.6642 | 0.43047 | 38 | 115 | 115 | 65.8614 | 263.4454 | 0.086093 | 55 | 57.5 | 57.5 | 9.6855 | 38.742 | 0 | 57.5 | 57.5 | 0 | 0 | 75.5469 | 302.1874
B2@180 | Holophane | SMST400MH00XXPM | 10 | 2 fixtures at 180 degrees | 10000 | 4304.6642 | 0.43047 | 76 | 230 | 230 | 131.7227 | 1317.2272 | 0.086093 | 110 | 115 | 115 | 19.371 | 193.7099 | 0 | 115 | 115 | 0 | 0 | 151.0937 | 1510.9371
C | Bega | 7275MH | 6 |  | 10000 | 4304.6642 | 0.43047 | 38 | 115 | 115 | 65.8614 | 395.1682 | 0.086093 | 55 | 57.5 | 57.5 | 9.6855 | 58.113 | 0 | 57.5 | 57.5 | 0 | 0 | 75.5469 | 453.2811
P | Holophane | SMST70MH00XXPM | 16 |  | 10000 | 4304.6642 | 0.43047 | 38 | 115 | 115 | 65.8614 | 1053.7818 | 0.086093 | 55 | 57.5 | 57.5 | 9.6855 | 154.9679 | 0 | 57.5 | 57.5 | 0 | 0 | 75.5469 | 1208.7497
W1 | Holophane | W4150MH00UX | 19 |  | 10000 | 4304.6642 | 0.43047 | 38 | 115 | 115 | 65.8614 | 1251.3659 | 0.086093 | 55 | 57.5 | 57.5 | 9.6855 | 184.0244 | 0 | 57.5 | 57.5 | 0 | 0 | 75.5469 | 1435.3903
W2 | Holophane | W435MH00UX | 1 |  | 10000 | 4304.6642 | 0.43047 | 38 | 115 | 115 | 65.8614 | 65.8614 | 0.086093 | 55 | 57.5 | 57.5 | 9.6855 | 9.6855 | 0 | 57.5 | 57.5 | 0 | 0 | 75.5469 | 75.5469
[11 empty] | Totals: | 5532.3544 | [5 empty] | 813.5815 |  |  |  |  | 0 |  | 6345.9359
College Ave (Roadway)
[7 empty] | Relamping |  |  | 0% |  |  | Replace Ballast |  |  | 0% |  |  | Fixture Cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
C2@180 | Holophane | 125 40S R3 DG | 3 | 2 fixtures at 180 degrees | 24000 | 4304.6642 | 0.17936 | 76 | 230 | 230 | 54.8845 | 164.6534 | 0.086093 | 110 | 115 | 115 | 19.371 | 58.113 | 0 | 115 | 115 | 0 | 0 | 74.2555 | 222.7664
[11 empty] | Totals: | 164.6534 | [5 empty] | 58.113 |  |  |  |  | 0 |  | 222.7664
College Ave (Area)
[7 empty] | Relamping |  |  | 0% |  |  | Replace Ballast |  |  | 0% |  |  | Fixture Cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
A | Spaulding Lighting | CE2-H1K-H3-F | 5 |  | 9000 | 4304.6642 | 0.4783 | 38 | 259.5 | 259.5 | 142.2931 | 711.4653 | 0.086093 | 55 | 129.75 | 129.75 | 15.9057 | 79.5287 | 0 | 129.75 | 129.75 | 0 | 0 | 158.1988 | 790.994
[11 empty] | Totals: | 711.4653 | [5 empty] | 79.5287 |  |  |  |  | 0 |  | 790.994
College Ave (Decorative)
[7 empty] | Relamping |  |  | 0% |  |  | Replace Ballast |  |  | 0% |  |  | Fixture Cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
B2@180 TWIN | Holophane | WA250MH00X4X4 | 10 | 2 fixtures at 180 degrees - twin | 10000 | 4304.6642 | 0.43047 | 76 | 230 | 230 | 131.7227 | 1317.2272 | 0.086093 | 110 | 115 | 115 | 19.371 | 193.7099 | 0 | 115 | 115 | 0 | 0 | 151.0937 | 1510.9371
[11 empty] | Totals: | 1317.2272 | [5 empty] | 193.7099 |  |  |  |  | 0 |  | 1510.9371
Note on I5: Valeria Holland: Average HID lamp cost from FSG
Note on I19: Valeria Holland: Average HID lamp cost from FSG
Note on I27: Valeria Holland: Average HID lamp cost from FSG
Note on I35: Valeria Holland: Average HID lamp cost from FSG
Note on J5: Labor costs taken from FSG
Note on J19: Labor costs taken from FSG
Note on J27: Labor costs taken from FSG
Note on J28: Valeria Holland: Labor cost + truck rental cost
Note on J35: Labor costs taken from FSG
Note on K5: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on K19: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on K27: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on K35: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on O5: Valeria Holland: Average ballast cost from FSG
Note on O19: Valeria Holland: Average ballast cost from FSG
Note on O27: Valeria Holland: Average ballast cost from FSG
Note on O35: Valeria Holland: Average ballast cost from FSG
Note on P5: Ballasts are replaced at the time of relamping, using 30 additional minutes, so only half of the relamping labor cost is incurred
Note on P19: Ballasts are replaced at the time of relamping, using 30 additional minutes, so only half of the relamping labor cost is incurred
Note on P27: Ballasts are replaced at the time of relamping, using 30 additional minutes, so only half of the relamping labor cost is incurred
Note on P35: Ballasts are replaced at the time of relamping, using 30 additional minutes, so only half of the relamping labor cost is incurred
Note on Q5: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on Q19: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on Q27: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on Q35: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on T5: According to FSG, the HID fixtures are almost never cleaned.
Note on T19: According to FSG, the HID fixtures are almost never cleaned.
Note on T27: According to FSG, the HID fixtures are almost never cleaned.
Note on T35: According to FSG, the HID fixtures are almost never cleaned.
Note on U5: Fixtures are cleaned at the time of relamping, using 30 additional minutes, so only half of the relamping labor cost is incurred
Note on U19: Fixtures are cleaned at the time of relamping, using 30 additional minutes, so only half of the relamping labor cost is incurred
Note on U27: Fixtures are cleaned at the time of relamping, using 30 additional minutes, so only half of the relamping labor cost is incurred
Note on U35: Fixtures are cleaned at the time of relamping, using 30 additional minutes, so only half of the relamping labor cost is incurred
Note on V5: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on V19: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on V27: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on V35: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.

## Maint_R1
ANNUAL Maintenance Cost - Retrofit Scenario 1 (RS1)
Model High School
[7 empty] | Replace fixture |  |  | 0% |  |  | Replace driver |  |  | 0% |  |  | Fixture cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
AR1 | Lithonia | RSX2 LED P6 40K R3 | 18 |  | 50000 | 4304.6642 | 0.0005 | 966.831 | 115 | 115 | 0.54092 | 9.7365 | 0.005 | 85 | 115 | 115 | 1 | 18 | 0 | 115 | 115 | 0 | 0 | 1.5409 | 27.7365
BR1 | Lithonia | RSX2 LED P6 40K R3 | 4 |  | 50000 | 4304.6642 | 0.0005 | 966.831 | 172 | 172 | 0.56942 | 2.2777 | 0.005 | 85 | 172 | 172 | 1.285 | 5.14 | 0 | 172 | 172 | 0 | 0 | 1.8544 | 7.4177
B2@180 R1 | Lithonia | RSX2 LED P6 40K R3 | 10 | 2 fixtures at 180 degrees | 50000 | 4304.6642 | 0.0005 | 1933.668 | 344 | 344 | 1.1388 | 11.3883 | 0.005 | 170 | 344 | 344 | 2.57 | 25.7 | 0 | 344 | 344 | 0 | 0 | 3.7088 | 37.0883
PR1 | Lithonia | DSX0 LED P1 40K 70CRI T2M | 16 |  | 50000 | 4304.6642 | 0.0005 | 1043.5637 | 90 | 90 | 0.56678 | 9.0685 | 0.005 | 85 | 90 | 90 | 0.875 | 14 | 0 | 90 | 90 | 0 | 0 | 1.4418 | 23.0685
W1R1 | Cree | C-WP-C-TR-S10L-SCCT-UL-DB | 19 |  | 50000 | 4304.6642 | 0.0005 | 241.923 | 90 | 90 | 0.16596 | 3.1533 | 0.005 | 85 | 90 | 90 | 0.875 | 16.625 | 0 | 90 | 90 | 0 | 0 | 1.041 | 19.7783
W2R1 | Cree | C-WP-C-TR-S6L-SCCT-UL-DB | 1 |  | 50000 | 4304.6642 | 0.0005 | 200.3656 | 90 | 90 | 0.14518 | 0.14518 | 0.005 | 85 | 90 | 90 | 0.875 | 0.875 | 0 | 90 | 90 | 0 | 0 | 1.0202 | 1.0202
CR1 | RAB | BLEDR24N | 6 |  | 50000 | 4304.6642 | 0.0005 | 1234.8461 | 202.5 | 202.5 | 0.71867 | 4.312 | 0.005 | 85 | 202.5 | 202.5 | 1.4375 | 8.625 | 0 | 202.5 | 202.5 | 0 | 0 | 2.1562 | 12.937
Controls | Acuity |  | 1
[11 empty] | Totals: | 40.0815 | [5 empty] | 88.965 |  |  |  |  | 0 |  | 129.0465
College Ave (Roadway)
[7 empty] | Replace fixture |  |  | 0% |  |  | Replace driver |  |  | 0% |  |  | Fixture cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
C2@180 R1 | Lithonia | ATRL G XXXXX R3 | 3 | 2 fixtures at 180 degrees | 50000 | 4304.6642 | 0.0005 | 1947.2573 | 230 | 230 | 1.0886 | 3.2659 | 0.005 | 170 | 230 | 230 | 2 | 6 | 0 | 230 | 230 | 0 | 0 | 3.0886 | 9.2659
Controls | Acuity |  | 1
[11 empty] | Totals: | 3.2659 | [5 empty] | 6 |  |  |  |  | 0 |  | 9.2659
College Ave (Area)
[7 empty] | Replace fixture |  |  | 0% |  |  | Replace driver |  |  | 0% |  |  | Fixture cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
AR1 | Lithonia | RSX4 LED P2 40K R3 | 5 |  | 50000 | 4304.6642 | 0.0005 | 1694.4997 | 259.5 | 259.5 | 0.977 | 4.885 | 0.005 | 85 | 259.5 | 259.5 | 1.7225 | 8.6125 | 0 | 259.5 | 259.5 | 0 | 0 | 2.6995 | 13.4975
Controls | Acuity |  | 1
[11 empty] | Totals: | 4.885 | [5 empty] | 8.6125 |  |  |  |  | 0 |  | 13.4975
College Ave (Decorative)
[7 empty] | Replace fixture |  |  | 0% |  |  | Replace driver |  |  | 0% |  |  | Fixture cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
B2@180 TWIN R1 | Holophane | AWDE3 P70 40K XXX AL5 | 10 | 2 fixtures at 180 degrees - twin | 50000 | 4304.6642 | 0.0005 | 2576.5538 | 230 | 230 | 1.4033 | 14.0328 | 0.005 | 170 | 230 | 230 | 2 | 20 | 0 | 230 | 230 | 0 | 0 | 3.4033 | 34.0328
Controls | Acuity |  | 1
[11 empty] | Totals: | 14.0328 | [5 empty] | 20 |  |  |  |  | 0 |  | 34.0328
Note on J5: Labor costs taken from FSG
Note on J20: Labor costs taken from FSG
Note on J29: Labor costs taken from FSG
Note on J30: Valeria Holland: Labor cost + truck rental cost
Note on J38: Labor costs taken from FSG
Note on K5: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on K20: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on K29: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on K38: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on O5: Valeria Holland: Average LED driver cost from FSG
Note on O20: Valeria Holland: Average LED driver cost from FSG
Note on O29: Valeria Holland: Average LED driver cost from FSG
Note on O38: Valeria Holland: Average LED driver cost from FSG
Note on P5: Labor costs taken from FSG
Note on P20: Labor costs taken from FSG
Note on P29: Labor costs taken from FSG
Note on P30: Valeria Holland: Labor cost + truck rental cost
Note on P38: Labor costs taken from FSG
Note on Q5: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on Q20: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on Q29: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on Q38: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on T5: According to FSG, the LED fixtures are almost never cleaned.
Note on T20: According to FSG, the LED fixtures are almost never cleaned.
Note on T29: According to FSG, the LED fixtures are almost never cleaned.
Note on T38: According to FSG, the LED fixtures are almost never cleaned.
Note on U5: Labor costs taken from FSG
Note on U20: Labor costs taken from FSG
Note on U29: Labor costs taken from FSG
Note on U30: Valeria Holland: Labor cost + truck rental cost
Note on U38: Labor costs taken from FSG
Note on V5: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on V20: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on V29: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on V38: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.

## Maint_R2
ANNUAL Maintenance Cost - Retrofit Scenario 1 (RS2)
Model High School
[7 empty] | Replace fixture |  |  | 0% |  |  | Replace driver |  |  | 0% |  |  | Fixture cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
AR2 | Lithonia | RSX2 LED P6 30K R3 | 13 |  | 50000 | 4304.6642 | 0.0005 | 966.831 | 115 | 115 | 0.54092 | 7.0319 | 0.005 | 85 | 115 | 115 | 1 | 13 | 0 | 115 | 115 | 0 | 0 | 1.5409 | 20.0319
AR2@180 | Lithonia | RSX2 LED P2 30K R3 | 2 | 2 fixtures at 180 degrees | 50000 | 4304.6642 | 0.0005 | 1725.6974 | 344 | 344 | 1.0348 | 2.0697 | 0.005 | 170 | 344 | 344 | 2.57 | 5.14 | 0 | 344 | 344 | 0 | 0 | 3.6048 | 7.2097
AR2@180_B | Lithonia | RSX2 LED P2 30K R3S | 1 | 2 fixtures at 180 degrees | 50000 | 4304.6642 | 0.0005 | 1725.6974 | 344 | 344 | 1.0348 | 1.0348 | 0.005 | 170 | 344 | 344 | 2.57 | 2.57 | 0 | 344 | 344 | 0 | 0 | 3.6048 | 3.6048
AR2_B | Lithonia | RSX2 LED P2 30K R3 | 5 |  | 50000 | 4304.6642 | 0.0005 | 862.8487 | 115 | 115 | 0.48892 | 2.4446 | 0.005 | 85 | 115 | 115 | 1 | 5 | 0 | 115 | 115 | 0 | 0 | 1.4889 | 7.4446
AR2_HS | Lithonia | RSX2 LED P2 30K R2 HS | 3 |  | 50000 | 4304.6642 | 0.0005 | 912.7768 | 172 | 172 | 0.54239 | 1.6272 | 0.005 | 85 | 172 | 172 | 1.285 | 3.855 | 0 | 172 | 172 | 0 | 0 | 1.8274 | 5.4822
B2@180 R2_B | Lithonia | RSX2 LED P4 30K R3 | 7 | 2 fixtures at 180 degrees | 50000 | 4304.6642 | 0.0005 | 1788.1224 | 344 | 344 | 1.0661 | 7.4624 | 0.005 | 170 | 344 | 344 | 2.57 | 17.99 | 0 | 344 | 344 | 0 | 0 | 3.6361 | 25.4524
BR2_B | Lithonia | RSX2 LED P4 30K R3 | 1 |  | 50000 | 4304.6642 | 0.0005 | 894.0612 | 172 | 172 | 0.53303 | 0.53303 | 0.005 | 85 | 172 | 172 | 1.285 | 1.285 | 0 | 172 | 172 | 0 | 0 | 1.818 | 1.818
PR2 | Lithonia | DSX0 LED P1 30K 70CRI T2M | 16 |  | 50000 | 4304.6642 | 0.0005 | 1043.5637 | 90 | 90 | 0.56678 | 9.0685 | 0.005 | 85 | 90 | 90 | 0.875 | 14 | 0 | 90 | 90 | 0 | 0 | 1.4418 | 23.0685
W1R2 | Cree | XSPW-B-WM-4ME-8L-30K-UL | 19 |  | 50000 | 4304.6642 | 0.0005 | 511.6003 | 90 | 90 | 0.3008 | 5.7152 | 0.005 | 85 | 90 | 90 | 0.875 | 16.625 | 0 | 90 | 90 | 0 | 0 | 1.1758 | 22.3402
W2R2 | Cree | XSPW-B-WM-4ME-2L-30K-UL | 1 |  | 50000 | 4304.6642 | 0.0005 | 511.6003 | 90 | 90 | 0.3008 | 0.3008 | 0.005 | 85 | 90 | 90 | 0.875 | 0.875 | 0 | 90 | 90 | 0 | 0 | 1.1758 | 1.1758
CR2 | Signify | PBL-14L-450-WW-G2-5-UNV | 6 |  | 50000 | 4304.6642 | 0.0005 | 1101.269 | 202.5 | 202.5 | 0.65188 | 3.9113 | 0.005 | 85 | 202.5 | 202.5 | 1.4375 | 8.625 | 0 | 202.5 | 202.5 | 0 | 0 | 2.0894 | 12.5363
Controls | Acuity |  | 1
[11 empty] | Totals: | 41.1995 | [5 empty] | 88.965 |  |  |  |  | 0 |  | 130.1645
College Ave (Roadway)
[7 empty] | Replace fixture |  |  | 0% |  |  | Replace driver |  |  | 0% |  |  | Fixture cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
C2@180 R2B | Cree | RSWX-B-HT-3ME-32L-30K7-Ux-xx-N | 3 | 2 fixtures at 180 degrees | 50000 | 4304.6642 | 0.0005 | 2894.1705 | 230 | 230 | 1.5621 | 4.6863 | 0.005 | 170 | 230 | 230 | 2 | 6 | 0 | 230 | 230 | 0 | 0 | 3.5621 | 10.6863
Controls | Acuity |  | 1
[11 empty] | Totals: | 4.6863 | [5 empty] | 6 |  |  |  |  | 0 |  | 10.6863
College Ave (Area)
[7 empty] | Replace fixture |  |  | 0% |  |  | Replace driver |  |  | 0% |  |  | Fixture cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
AR2 | Lithonia | RSX4 LED P3 30K R3 | 5 |  | 50000 | 4304.6642 | 0.0005 | 1694.4997 | 259.5 | 259.5 | 0.977 | 4.885 | 0.005 | 85 | 259.5 | 259.5 | 1.7225 | 8.6125 | 0 | 259.5 | 259.5 | 0 | 0 | 2.6995 | 13.4975
Controls | Acuity |  | 1
[11 empty] | Totals: | 4.885 | [5 empty] | 8.6125 |  |  |  |  | 0 |  | 13.4975
College Ave (Decorative)
[7 empty] | Replace fixture |  |  | 0% |  |  | Replace driver |  |  | 0% |  |  | Fixture cleaning |  | 0% |  |  | Total Costs
Type | Manufacturer | Catalog Number | Quantity | Notes | Estimated Life (hrs) | Operating Hours | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/Yr | Material Cost | Labor cost | +Labor markup | UNIT Cost | QTY Cost | Freq/yr | Labor cost | +Labor markup | UNIT Cost | QTY Cost | UNIT | QTY
B2@180 TWIN R2 | Signify | RN30-145W64LED3K-G3-LE5F | 10 | 2 fixtures at 180 degrees - twin | 50000 | 4304.6642 | 0.0005 | 3940.5244 | 230 | 230 | 2.0853 | 20.8526 | 0.005 | 170 | 230 | 230 | 2 | 20 | 0 | 230 | 230 | 0 | 0 | 4.0853 | 40.8526
Controls | Acuity |  | 1
[11 empty] | Totals: | 20.8526 | [5 empty] | 20 |  |  |  |  | 0 |  | 40.8526
Note on J5: Labor costs taken from FSG
Note on J24: Labor costs taken from FSG
Note on J33: Labor costs taken from FSG
Note on J34: Valeria Holland: Labor cost + truck rental cost
Note on J42: Labor costs taken from FSG
Note on K5: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on K24: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on K33: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on K42: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on O5: Valeria Holland: Average LED driver cost from FSG
Note on O24: Valeria Holland: Average LED driver cost from FSG
Note on O33: Valeria Holland: Average LED driver cost from FSG
Note on O42: Valeria Holland: Average LED driver cost from FSG
Note on P5: Labor costs taken from FSG
Note on P24: Labor costs taken from FSG
Note on P33: Labor costs taken from FSG
Note on P34: Valeria Holland: Labor cost + truck rental cost
Note on P42: Labor costs taken from FSG
Note on Q5: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on Q24: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on Q33: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on Q42: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on T5: According to FSG, the LED fixtures are almost never cleaned.
Note on T24: According to FSG, the LED fixtures are almost never cleaned.
Note on T33: According to FSG, the LED fixtures are almost never cleaned.
Note on T42: According to FSG, the LED fixtures are almost never cleaned.
Note on U5: Labor costs taken from FSG
Note on U24: Labor costs taken from FSG
Note on U33: Labor costs taken from FSG
Note on U34: Valeria Holland: Labor cost + truck rental cost
Note on U42: Labor costs taken from FSG
Note on V5: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on V24: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on V33: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.
Note on V42: Labor costs taken from RS Means include labor markups that vary by product type. This column is included to allow the application of a uniform labor markup.

## Maint_Summary (Ref)
Maintenance Cost - SUMMARY
| Yearly Maintenance Cost |  |  |  |  | Yearly Maintenance Cost | [8 empty] | Lifetime Maintenance Cost
|  | Base Case |  |  |  |  | Retrofit 1 |  |  |  | Retrofit 2 |  |  |  |  | Retrofit 1 |  |  |  |  | Retrofit 2
| Site | Relamp | Ballast | Clean | Total | Site | Replace | Driver | Clean | Total | Replace | Driver | Clean | Total | Site | Replace | Driver | Clean | Total |  | Replace | Driver | Clean | Total
| Model High School | 5532.3544 | 813.5815 | 0 | 6345.9359 | Model High School | 40.0815 | 88.965 | 0 | 129.0465 | 41.1995 | 88.965 | 0 | 130.1645 | Model High School | 801.6296 | 1779.3 | 0 | 2580.9296 | 0 | 823.9903 | 1779.3 | 0 | 2603.2903
| College Ave (Roadway) | 164.6534 | 58.113 | 0 | 222.7664 | College Ave (Roadway) | 3.2659 | 6 | 0 | 9.2659 | 4.6863 | 6 | 0 | 10.6863 | College Ave (Roadway) | 65.3177 | 120 | 0 | 185.3177 | 0 | 93.7251 | 120 | 0 | 213.7251
| College Ave (Area) | 711.4653 | 79.5287 | 0 | 790.994 | College Ave (Area) | 4.885 | 8.6125 | 0 | 13.4975 | 4.885 | 8.6125 | 0 | 13.4975 | College Ave (Area) | 97.7 | 172.25 | 0 | 269.95 | 0 | 97.7 | 172.25 | 0 | 269.95
| College Ave (Decorative) | 1317.2272 | 193.7099 | 0 | 1510.9371 | College Ave (Decorative) | 14.0328 | 20 | 0 | 34.0328 | 14.0328 | 20 | 0 | 40.8526 | College Ave (Decorative) | 280.6554 | 400 | 0 | 680.6554 | 0 | 280.6554 | 400 | 0 | 817.0524

## Energy
ANNUAL Energy Cost (and cost savings) Calculations
Model High School - Base Case
|  | Adjusted hours (Hours * Load Shed Lvl) |  |  | Annual Energy Consumption (kWh) |  |  | Annual Energy Cost ($) |  |  | Annual Energy Cost Savings | Lifecycle Energy Cost Savings
Scenario | Power (kW) | Summer | Winter | Total | Summer | Winter | Total | Summer | Winter | Total | (Relative to Base Case) | (Relative to Base Case)
Model High School - Base Case | 24.409 | 1220.7131 | 3083.9511 | 43485.6 | 29796.385 | 75276.1627 | 105072.5476 | 3191.1928 | 9093.3605 | 12284.5533 | 0 | 0
Model High School - Retrofit 1 (50% dim) | 12.348 | 852.9564 | 2255.4703 | 39180.9358 | 10532.3055 | 27850.547 | 38382.8525 | 1128.0099 | 3364.3461 | 4492.356 | 7792.1973 | 155843.9457
Model High School - Retrofit 2 (80% dim) | 9.806 | 632.3024 | 1758.3818 | 36072.5092 | 6200.3572 | 17242.6917 | 23443.0489 | 664.0583 | 2082.9172 | 2746.9754 | 9537.5779 | 190751.5573
College Ave (Roadway) - Base Case | 2.76 | 1220.7131 | 3083.9511 | 33681.825 | 3369.168 | 8511.7051 | 11880.8731 | 360.8379 | 1028.214 | 1389.0519 | 0 | 0
College Ave (Roadway) - Retrofit 1 (50% dim) | 1.674 | 1035.9564 | 2619.9703 | 29377.1608 | 1734.191 | 4385.8302 | 6120.0212 | 185.7319 | 529.8083 | 715.5401 | 673.5117 | 13470.2344
College Ave (Roadway) - Retrofit 2 (80% dim) | 1.488 | 925.1024 | 2341.5818 | 25721.2342 | 1376.5524 | 3484.2737 | 4860.826 | 147.4288 | 420.9003 | 568.329 | 820.7229 | 16414.457
College Ave (Area) - Base Case | 5.4 | 1220.7131 | 3083.9511 | 22454.55 | 6591.8505 | 16653.336 | 23245.1865 | 705.9872 | 2011.723 | 2717.7102 | 0 | 0
College Ave (Area) - Retrofit 1 (50% dim) | 1.6 | 1035.9564 | 2619.9703 | 18149.8858 | 1657.5302 | 4191.9524 | 5849.4827 | 177.5215 | 506.3879 | 683.9093 | 2033.8008 | 40676.0167
College Ave (Area) - Retrofit 2 (80% dim) | 1.845 | 925.1024 | 2341.5818 | 14493.9592 | 1706.8139 | 4320.2184 | 6027.0323 | 182.7998 | 521.8824 | 704.6821 | 2013.028 | 40260.5606
College Ave (Decorative) - Base Case | 5.66 | 1220.7131 | 3083.9511 | 11227.275 | 6909.2359 | 17455.1633 | 24364.3992 | 739.9792 | 2108.5837 | 2848.5629 | 0 | 0
College Ave (Decorative) - Retrofit 1 (50% dim) | 3.12 | 1035.9564 | 2619.9703 | 6922.6108 | 3232.1839 | 8174.3073 | 11406.4912 | 346.1669 | 987.4563 | 1333.6232 | 1514.9397 | 30298.7935
College Ave (Decorative) - Retrofit 2 (80% dim) | 2.8 | 925.1024 | 2341.5818 | 3266.6842 | 2590.2867 | 6556.429 | 9146.7157 | 277.4197 | 792.0166 | 1069.4363 | 1779.1266 | 35582.5313
Axis Labels ---------------->
Model High School - Base Case
Model High School - Retrofit 1 (50% dim)
Model High School - Retrofit 2 (80% dim)
College Ave (Roadway) - Base Case
College Ave (Roadway) - Retrofit 1 (50% dim)
College Ave (Roadway) - Retrofit 2 (80% dim)
College Ave (Area) - Base Case
College Ave (Area) - Retrofit 1 (50% dim)
College Ave (Area) - Retrofit 2 (80% dim)
College Ave (Decorative) - Base Case
College Ave (Decorative) - Retrofit 1 (50% dim)
College Ave (Decorative) - Retrofit 2 (80% dim)

## Rebates
Rebate Calculations
| Xcel Rebates/Incentives (6-8 weeks after installing) |  |  |  | Xcel Rebate |  |  | Fort Collins Utility Rebate
| Area fixtures | Per Fixture (Non-DLC) | Per Fixture (DLC) | Scenario | Fixtures | Controls | Total | Fixtures | Controls | Total | Editable Fields for Fort Collins Utility Rebate
| 45W-65W | 26.25 | 35 | Model High School - Retrofit 1 (50% dim) | 5305 | 4939.2 | 10244.2 | 15076.25 | 6174 | 21250.25
| 66W-89W | 26.25 | 35 | Model High School - Retrofit 2 (80% dim) | 4155 | 3922.4 | 8077.4 | 18253.75 | 4903 | 23156.75 | Fixture: | 1.25 | per Watt of reduced load
| 90W-119W | 30 | 40 | College Ave (Roadway) - Retrofit 1 (50% dim) | 300 | 669.6 | 969.6 | 1357.5 | 837 | 2194.5 | Controls: | 0.5 | per Watt of controlled load
| 120W-140W | 37.5 | 50 | College Ave (Roadway) - Retrofit 2 (80% dim) | 300 | 595.2 | 895.2 | 1590 | 744 | 2334
| 141W-199W | 45 | 60 | College Ave (Area) - Retrofit 1 (50% dim) | 250 | 640 | 890 | 4750 | 800 | 5550
| 200W-550W | 67.5 | 90 | College Ave (Area) - Retrofit 2 (80% dim) | 250 | 738 | 988 | 4443.75 | 922.5 | 5366.25
|  |  |  | College Ave (Decorative) - Retrofit 1 (50% dim) | 1000 | 1248 | 2248 | 3175 | 1560 | 4735
| Street fixtures | Per Fixture (Non-DLC) | Per Fixture (DLC) | College Ave (Decorative) - Retrofit 2 (80% dim) | 1000 | 1120 | 2120 | 3575 | 1400 | 4975
| 55W-79W | 18.75 | 25
| 80W-109W | 18.75 | 25
| 110W-139W | 30 | 40
| 140W-209W | 37.5 | 50 | Axis Labels --------------------------------------->
Model High School - Retrofit 1 (50% dim)
| Wallpacks | Per Fixture (Non-DLC) | Per Fixture (DLC) | Model High School - Retrofit 2 (80% dim)
| 10W-25W | 11.25 | 15 | College Ave (Roadway) - Retrofit 1 (50% dim)
| 26W-60W | 22.5 | 30 | College Ave (Roadway) - Retrofit 2 (80% dim)
| 61W-150W | 37.5 | 50 | College Ave (Area) - Retrofit 1 (50% dim)
College Ave (Area) - Retrofit 2 (80% dim)
College Ave (Decorative) - Retrofit 1 (50% dim)
College Ave (Decorative) - Retrofit 2 (80% dim)
Note on G7: Rebate for fixtures is a fixed amount that is determined by the type of fixture and it's power consumption
Note on H7: Control rebate is $0.40 per Watt of controlled load.
Note on K7: Rebate for fixtures is $1.25 per Watt of reduced load.
Note on L7: Control rebate is $0.50 per Watt of controlled load.

## ROI (ref)
Payback and ROI calculations
| Capital Cost ($) |  |  | Rebates ($) |  |  | Capital Cost Less Rebates ($) | Annual Maintenance Cost ($) |  |  |  | Annual Energy Cost ($) |  |  | Annual Cost Savings (Relative to Base) |  |  | Payback period
Scenario | Material | Installation | Total | Fixtures | Controls | Total |  | Relamp/Replace | Ballast/Driver | Clean | Total | Summer | Winter | Total | Maintenance | Energy | Total | (Years) | ROI
Model High School - Base Case | [7 empty] | 5532.3544 | 813.5815 | 0 | 6345.9359 | 3191.1928 | 9093.3605 | 12284.5533
Model High School - Retrofit 1 (50% dim) | 89746.8914 | 11113 | 100859.8914 | 15076.25 | 6174 | 21250.25 | 79609.6414 | 40.0815 | 88.965 | 0 | 129.0465 | 1128.0099 | 3364.3461 | 4492.356 | 6216.8894 | 7792.1973 | 14009.0867 | 5.6827 | 17.6%
Model High School - Retrofit 2 (80% dim) | 91982.9572 | 11113 | 103095.9572 | 18253.75 | 4903 | 23156.75 | 79939.2072 | 41.1995 | 88.965 | 0 | 130.1645 | 664.0583 | 2082.9172 | 2746.9754 | 6215.7714 | 9537.5779 | 15753.3493 | 5.0744 | 19.71%
College Ave (Roadway) - Base Case | [7 empty] | 164.6534 | 58.113 | 0 | 222.7664 | 360.8379 | 1028.214 | 1389.0519
College Ave (Roadway) - Retrofit 1 (50% dim) | 12452.9626 | 1150 | 13602.9626 | 1357.5 | 837 | 2194.5 | 11408.4626 | 3.2659 | 6 | 0 | 9.2659 | 185.7319 | 529.8083 | 715.5401 | 213.5005 | 673.5117 | 887.0122 | 12.8617 | 7.775%
College Ave (Roadway) - Retrofit 2 (80% dim) | 15293.7023 | 1150 | 16443.7023 | 1590 | 744 | 2334 | 14109.7023 | 4.6863 | 6 | 0 | 10.6863 | 147.4288 | 420.9003 | 568.329 | 212.0801 | 820.7229 | 1032.803 | 13.6616 | 7.32%
College Ave (Area) - Base Case | [7 empty] | 711.4653 | 79.5287 | 0 | 790.994 | 705.9872 | 2011.723 | 2717.7102
College Ave (Area) - Retrofit 1 (50% dim) | 14610.4703 | 1757.5 | 16367.9703 | 4750 | 800 | 5550 | 10817.9703 | 4.885 | 8.6125 | 0 | 13.4975 | 177.5215 | 506.3879 | 683.9093 | 777.4965 | 2033.8008 | 2811.2973 | 3.848 | 25.99%
College Ave (Area) - Retrofit 2 (80% dim) | 14610.4703 | 1757.5 | 16367.9703 | 4443.75 | 922.5 | 5366.25 | 11001.7203 | 4.885 | 8.6125 | 0 | 13.4975 | 182.7998 | 521.8824 | 704.6821 | 777.4965 | 2013.028 | 2790.5245 | 3.9425 | 25.36%
College Ave (Decorative) - Base Case | [7 empty] | 1317.2272 | 193.7099 | 0 | 1510.9371 | 739.9792 | 2108.5837 | 2848.5629
College Ave (Decorative) - Retrofit 1 (50% dim) | 32750.3889 | 2760 | 35510.3889 | 3175 | 1560 | 4735 | 30775.3889 | 14.0328 | 20 | 0 | 34.0328 | 346.1669 | 987.4563 | 1333.6232 | 1476.9044 | 1514.9397 | 2991.844 | 10.2864 | 9.722%
College Ave (Decorative) - Retrofit 2 (80% dim) | 46390.095 | 2760 | 49150.095 | 3575 | 1400 | 4975 | 44175.095 | 20.8526 | 20 | 0 | 40.8526 | 277.4197 | 792.0166 | 1069.4363 | 1470.0845 | 1779.1266 | 3249.2111 | 13.5956 | 7.355%

## OpHrs (Ref)
ANNUAL operating hours - Calculations
SunEarthTools.com | [19 empty] | Midnight | 3am
coordinates: 40.5853804, -105.0847024 | [19 empty] | 24:00 | 3:00
location: 40.76000000,-73.98400000
2023-01-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn | 2023-02-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn | 2023-03-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn | 2023-04-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn
Date | Sunrise | Sunset | [5 empty] | Date | Sunrise | Sunset | [5 empty] | Date | Sunrise | Sunset | [5 empty] | Date | Sunrise | Sunset
01 Sun | 7:24 | 16:44 | 14:40 | 7:16 | 7:24 | 10:16 | 4:24 | 01 Wed | 7:10 | 17:18 | 13:52 | 6:42 | 7:10 | 9:42 | 4:10 | 01 Wed | 6:34 | 17:52 | 12:43 | 6:08 | 6:34 | 9:08 | 3:34 | 01 Sat | 6:44 | 19:25 | 11:19 | 4:35 | 6:44 | 7:35 | 3:44
02 Mon | 7:24 | 16:45 | 14:39 | 7:15 | 7:24 | 10:15 | 4:24 | 02 Thu | 7:09 | 17:19 | 13:50 | 6:41 | 7:09 | 9:41 | 4:09 | 02 Thu | 6:33 | 17:53 | 12:40 | 6:07 | 6:33 | 9:07 | 3:33 | 02 Sun | 6:43 | 19:26 | 11:17 | 4:34 | 6:43 | 7:34 | 3:43
03 Tue | 7:24 | 16:46 | 14:38 | 7:14 | 7:24 | 10:14 | 4:24 | 03 Fri | 7:08 | 17:21 | 13:48 | 6:39 | 7:08 | 9:39 | 4:08 | 03 Fri | 6:31 | 17:54 | 12:37 | 6:06 | 6:31 | 9:06 | 3:31 | 03 Mon | 6:41 | 19:27 | 11:14 | 4:33 | 6:41 | 7:33 | 3:41
04 Wed | 7:24 | 16:47 | 14:38 | 7:13 | 7:24 | 10:13 | 4:24 | 04 Sat | 7:07 | 17:22 | 13:45 | 6:38 | 7:07 | 9:38 | 4:07 | 04 Sat | 6:30 | 17:55 | 12:35 | 6:05 | 6:30 | 9:05 | 3:30 | 04 Tue | 6:39 | 19:28 | 11:11 | 4:32 | 6:39 | 7:32 | 3:39
05 Thu | 7:24 | 16:48 | 14:37 | 7:12 | 7:24 | 10:12 | 4:24 | 05 Sun | 7:06 | 17:23 | 13:43 | 6:37 | 7:06 | 9:37 | 4:06 | 05 Sun | 6:28 | 17:56 | 12:32 | 6:04 | 6:28 | 9:04 | 3:28 | 05 Wed | 6:38 | 19:29 | 11:09 | 4:31 | 6:38 | 7:31 | 3:38
06 Fri | 7:24 | 16:49 | 14:36 | 7:11 | 7:24 | 10:11 | 4:24 | 06 Mon | 7:05 | 17:24 | 13:41 | 6:36 | 7:05 | 9:36 | 4:05 | 06 Mon | 6:27 | 17:57 | 12:29 | 6:03 | 6:27 | 9:03 | 3:27 | 06 Thu | 6:36 | 19:30 | 11:06 | 4:30 | 6:36 | 7:30 | 3:36
07 Sat | 7:24 | 16:50 | 14:35 | 7:10 | 7:24 | 10:10 | 4:24 | 07 Tue | 7:04 | 17:26 | 13:38 | 6:34 | 7:04 | 9:34 | 4:04 | 07 Tue | 6:25 | 17:58 | 12:27 | 6:02 | 6:25 | 9:02 | 3:25 | 07 Fri | 6:34 | 19:31 | 11:03 | 4:29 | 6:34 | 7:29 | 3:34
08 Sun | 7:24 | 16:50 | 14:33 | 7:10 | 7:24 | 10:10 | 4:24 | 08 Wed | 7:03 | 17:27 | 13:36 | 6:33 | 7:03 | 9:33 | 4:03 | 08 Wed | 6:23 | 17:59 | 12:24 | 6:01 | 6:23 | 9:01 | 3:23 | 08 Sat | 6:33 | 19:32 | 11:01 | 4:28 | 6:33 | 7:28 | 3:33
09 Mon | 7:24 | 16:52 | 14:32 | 7:08 | 7:24 | 10:08 | 4:24 | 09 Thu | 7:02 | 17:28 | 13:34 | 6:32 | 7:02 | 9:32 | 4:02 | 09 Thu | 6:22 | 18:01 | 12:21 | 5:59 | 6:22 | 8:59 | 3:22 | 09 Sun | 6:31 | 19:33 | 10:58 | 4:27 | 6:31 | 7:27 | 3:31
10 Tue | 7:24 | 16:53 | 14:31 | 7:07 | 7:24 | 10:07 | 4:24 | 10 Fri | 7:00 | 17:29 | 13:31 | 6:31 | 7:00 | 9:31 | 4:00 | 10 Fri | 6:20 | 18:02 | 12:19 | 5:58 | 6:20 | 8:58 | 3:20 | 10 Mon | 6:30 | 19:34 | 10:55 | 4:26 | 6:30 | 7:26 | 3:30
11 Wed | 7:23 | 16:54 | 14:30 | 7:06 | 7:23 | 10:06 | 4:23 | 11 Sat | 6:59 | 17:30 | 13:29 | 6:30 | 6:59 | 9:30 | 3:59 | 11 Sat | 6:19 | 18:03 | 12:16 | 5:57 | 6:19 | 8:57 | 3:19 | 11 Tue | 6:28 | 19:35 | 10:53 | 4:25 | 6:28 | 7:25 | 3:28
12 Thu | 7:23 | 16:55 | 14:28 | 7:05 | 7:23 | 10:05 | 4:23 | 12 Sun | 6:58 | 17:32 | 13:26 | 6:28 | 6:58 | 9:28 | 3:58 | 12 Sun | 7:17 | 19:04 | 12:13 | 4:56 | 7:17 | 7:56 | 4:17 | 12 Wed | 6:27 | 19:36 | 10:50 | 4:24 | 6:27 | 7:24 | 3:27
13 Fri | 7:23 | 16:56 | 14:27 | 7:04 | 7:23 | 10:04 | 4:23 | 13 Mon | 6:57 | 17:33 | 13:24 | 6:27 | 6:57 | 9:27 | 3:57 | 13 Mon | 7:15 | 19:05 | 12:11 | 4:55 | 7:15 | 7:55 | 4:15 | 13 Thu | 6:25 | 19:37 | 10:48 | 4:23 | 6:25 | 7:23 | 3:25
14 Sat | 7:22 | 16:57 | 14:26 | 7:03 | 7:22 | 10:03 | 4:22 | 14 Tue | 6:55 | 17:34 | 13:21 | 6:26 | 6:55 | 9:26 | 3:55 | 14 Tue | 7:14 | 19:06 | 12:08 | 4:54 | 7:14 | 7:54 | 4:14 | 14 Fri | 6:23 | 19:38 | 10:45 | 4:22 | 6:23 | 7:22 | 3:23
15 Sun | 7:22 | 16:58 | 14:24 | 7:02 | 7:22 | 10:02 | 4:22 | 15 Wed | 6:54 | 17:35 | 13:19 | 6:25 | 6:54 | 9:25 | 3:54 | 15 Wed | 7:12 | 19:07 | 12:05 | 4:53 | 7:12 | 7:53 | 4:12 | 15 Sat | 6:22 | 19:40 | 10:42 | 4:20 | 6:22 | 7:20 | 3:22
16 Mon | 7:22 | 16:59 | 14:22 | 7:01 | 7:22 | 10:01 | 4:22 | 16 Thu | 6:53 | 17:36 | 13:16 | 6:24 | 6:53 | 9:24 | 3:53 | 16 Thu | 7:10 | 19:08 | 12:02 | 4:52 | 7:10 | 7:52 | 4:10 | 16 Sun | 6:20 | 19:41 | 10:40 | 4:19 | 6:20 | 7:19 | 3:20
17 Tue | 7:21 | 17:00 | 14:21 | 7:00 | 7:21 | 10:00 | 4:21 | 17 Fri | 6:52 | 17:38 | 13:14 | 6:22 | 6:52 | 9:22 | 3:52 | 17 Fri | 7:09 | 19:09 | 12:00 | 4:51 | 7:09 | 7:51 | 4:09 | 17 Mon | 6:19 | 19:42 | 10:37 | 4:18 | 6:19 | 7:18 | 3:19
18 Wed | 7:21 | 17:01 | 14:19 | 6:59 | 7:21 | 9:59 | 4:21 | 18 Sat | 6:50 | 17:39 | 13:11 | 6:21 | 6:50 | 9:21 | 3:50 | 18 Sat | 7:07 | 19:10 | 11:57 | 4:50 | 7:07 | 7:50 | 4:07 | 18 Tue | 6:17 | 19:43 | 10:35 | 4:17 | 6:17 | 7:17 | 3:17
19 Thu | 7:20 | 17:03 | 14:18 | 6:58 | 7:20 | 9:58 | 4:20 | 19 Sun | 6:49 | 17:40 | 13:09 | 6:20 | 6:49 | 9:20 | 3:49 | 19 Sun | 7:06 | 19:11 | 11:54 | 4:49 | 7:06 | 7:49 | 4:06 | 19 Wed | 6:16 | 19:44 | 10:32 | 4:16 | 6:16 | 7:16 | 3:16
20 Fri | 7:19 | 17:04 | 14:16 | 6:56 | 7:19 | 9:56 | 4:19 | 20 Mon | 6:47 | 17:41 | 13:06 | 6:19 | 6:47 | 9:19 | 3:47 | 20 Mon | 7:04 | 19:12 | 11:52 | 4:48 | 7:04 | 7:48 | 4:04 | 20 Thu | 6:14 | 19:45 | 10:30 | 4:15 | 6:14 | 7:15 | 3:14
21 Sat | 7:19 | 17:05 | 14:14 | 6:55 | 7:19 | 9:55 | 4:19 | 21 Tue | 6:46 | 17:42 | 13:04 | 6:18 | 6:46 | 9:18 | 3:46 | 21 Tue | 7:02 | 19:13 | 11:49 | 4:47 | 7:02 | 7:47 | 4:02 | 21 Fri | 6:13 | 19:46 | 10:27 | 4:14 | 6:13 | 7:14 | 3:13
22 Sun | 7:18 | 17:06 | 14:12 | 6:54 | 7:18 | 9:54 | 4:18 | 22 Wed | 6:45 | 17:44 | 13:01 | 6:16 | 6:45 | 9:16 | 3:45 | 22 Wed | 7:01 | 19:14 | 11:46 | 4:46 | 7:01 | 7:46 | 4:01 | 22 Sat | 6:12 | 19:47 | 10:25 | 4:13 | 6:12 | 7:13 | 3:12
23 Mon | 7:18 | 17:07 | 14:10 | 6:53 | 7:18 | 9:53 | 4:18 | 23 Thu | 6:43 | 17:45 | 12:58 | 6:15 | 6:43 | 9:15 | 3:43 | 23 Thu | 6:59 | 19:16 | 11:43 | 4:44 | 6:59 | 7:44 | 3:59 | 23 Sun | 6:10 | 19:48 | 10:22 | 4:12 | 6:10 | 7:12 | 3:10
24 Tue | 7:17 | 17:08 | 14:08 | 6:52 | 7:17 | 9:52 | 4:17 | 24 Fri | 6:42 | 17:46 | 12:56 | 6:14 | 6:42 | 9:14 | 3:42 | 24 Fri | 6:57 | 19:17 | 11:41 | 4:43 | 6:57 | 7:43 | 3:57 | 24 Mon | 6:09 | 19:49 | 10:20 | 4:11 | 6:09 | 7:11 | 3:09
25 Wed | 7:16 | 17:10 | 14:06 | 6:50 | 7:16 | 9:50 | 4:16 | 25 Sat | 6:40 | 17:47 | 12:53 | 6:13 | 6:40 | 9:13 | 3:40 | 25 Sat | 6:56 | 19:18 | 11:38 | 4:42 | 6:56 | 7:42 | 3:56 | 25 Tue | 6:07 | 19:50 | 10:17 | 4:10 | 6:07 | 7:10 | 3:07
26 Thu | 7:15 | 17:11 | 14:05 | 6:49 | 7:15 | 9:49 | 4:15 | 26 Sun | 6:39 | 17:48 | 12:51 | 6:12 | 6:39 | 9:12 | 3:39 | 26 Sun | 6:54 | 19:19 | 11:35 | 4:41 | 6:54 | 7:41 | 3:54 | 26 Wed | 6:06 | 19:51 | 10:15 | 4:09 | 6:06 | 7:09 | 3:06
27 Fri | 7:15 | 17:12 | 14:03 | 6:48 | 7:15 | 9:48 | 4:15 | 27 Mon | 6:37 | 17:49 | 12:48 | 6:11 | 6:37 | 9:11 | 3:37 | 27 Mon | 6:52 | 19:20 | 11:33 | 4:40 | 6:52 | 7:40 | 3:52 | 27 Thu | 6:05 | 19:52 | 10:13 | 4:08 | 6:05 | 7:08 | 3:05
28 Sat | 7:14 | 17:13 | 14:00 | 6:47 | 7:14 | 9:47 | 4:14 | 28 Tue | 6:36 | 17:50 | 12:45 | 6:10 | 6:36 | 9:10 | 3:36 | 28 Tue | 6:51 | 19:21 | 11:30 | 4:39 | 6:51 | 7:39 | 3:51 | 28 Fri | 6:03 | 19:53 | 10:10 | 4:07 | 6:03 | 7:07 | 3:03
29 Sun | 7:13 | 17:15 | 13:58 | 6:45 | 7:13 | 9:45 | 4:13 |  |  | Total | 373:09 | 179:53 | 193:17 | 263:53 | 109:17 | 29 Wed | 6:49 | 19:22 | 11:27 | 4:38 | 6:49 | 7:38 | 3:49 | 29 Sat | 6:02 | 19:54 | 10:08 | 4:06 | 6:02 | 7:06 | 3:02
30 Mon | 7:12 | 17:16 | 13:56 | 6:44 | 7:12 | 9:44 | 4:12 | [8 empty] | 30 Thu | 6:47 | 19:23 | 11:25 | 4:37 | 6:47 | 7:37 | 3:47 | 30 Sun | 6:01 | 19:55 | 10:06 | 4:05 | 6:01 | 7:05 | 3:01
31 Tue | 7:11 | 17:17 | 13:54 | 6:43 | 7:11 | 9:43 | 4:11 | [8 empty] | 31 Fri | 6:46 | 19:24 | 11:22 | 4:36 | 6:46 | 7:36 | 3:46 |  |  | Total | 320:47 | 129:59 | 190:49 | 219:59 | 100:49
|  | Total | 444:36 | 217:14 | 227:23 | 310:14 | 134:23 | [10 empty] | Total | 373:13 | 161:53 | 211:21 | 254:53 | 118:21
2023-05-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn | 2023-06-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn | 2023-07-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn | 2023-08-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn
Date | Sunrise | Sunset | [5 empty] | Date | Sunrise | Sunset | [5 empty] | Date | Sunrise | Sunset | [5 empty] | Date | Sunrise | Sunset
01 Mon | 5:59 | 19:56 | 10:03 | 4:04 | 5:59 | 7:04 | 2:59 | 01 Thu | 5:32 | 20:25 | 9:07 | 3:35 | 5:32 | 6:35 | 2:32 | 01 Sat | 5:33 | 20:35 | 8:58 | 3:25 | 5:33 | 6:25 | 2:33 | 01 Tue | 5:57 | 20:16 | 9:42 | 3:44 | 5:57 | 6:44 | 2:57
02 Tue | 5:58 | 19:57 | 10:01 | 4:03 | 5:58 | 7:03 | 2:58 | 02 Fri | 5:31 | 20:26 | 9:06 | 3:34 | 5:31 | 6:34 | 2:31 | 02 Sun | 5:34 | 20:35 | 8:59 | 3:25 | 5:34 | 6:25 | 2:34 | 02 Wed | 5:58 | 20:14 | 9:44 | 3:46 | 5:58 | 6:46 | 2:58
03 Wed | 5:57 | 19:58 | 9:59 | 4:02 | 5:57 | 7:02 | 2:57 | 03 Sat | 5:31 | 20:26 | 9:05 | 3:34 | 5:31 | 6:34 | 2:31 | 03 Mon | 5:34 | 20:35 | 9:00 | 3:25 | 5:34 | 6:25 | 2:34 | 03 Thu | 5:59 | 20:13 | 9:46 | 3:47 | 5:59 | 6:47 | 2:59
04 Thu | 5:56 | 19:59 | 9:56 | 4:01 | 5:56 | 7:01 | 2:56 | 04 Sun | 5:31 | 20:27 | 9:04 | 3:33 | 5:31 | 6:33 | 2:31 | 04 Tue | 5:35 | 20:35 | 9:00 | 3:25 | 5:35 | 6:25 | 2:35 | 04 Fri | 6:00 | 20:12 | 9:48 | 3:48 | 6:00 | 6:48 | 3:00
05 Fri | 5:54 | 20:00 | 9:54 | 4:00 | 5:54 | 7:00 | 2:54 | 05 Mon | 5:30 | 20:28 | 9:03 | 3:32 | 5:30 | 6:32 | 2:30 | 05 Wed | 5:35 | 20:34 | 9:01 | 3:26 | 5:35 | 6:26 | 2:35 | 05 Sat | 6:01 | 20:11 | 9:50 | 3:49 | 6:01 | 6:49 | 3:01
06 Sat | 5:53 | 20:01 | 9:52 | 3:59 | 5:53 | 6:59 | 2:53 | 06 Tue | 5:30 | 20:28 | 9:02 | 3:32 | 5:30 | 6:32 | 2:30 | 06 Thu | 5:36 | 20:34 | 9:02 | 3:26 | 5:36 | 6:26 | 2:36 | 06 Sun | 6:02 | 20:10 | 9:52 | 3:50 | 6:02 | 6:50 | 3:02
07 Sun | 5:52 | 20:02 | 9:50 | 3:58 | 5:52 | 6:58 | 2:52 | 07 Wed | 5:30 | 20:29 | 9:01 | 3:31 | 5:30 | 6:31 | 2:30 | 07 Fri | 5:37 | 20:34 | 9:03 | 3:26 | 5:37 | 6:26 | 2:37 | 07 Mon | 6:03 | 20:09 | 9:54 | 3:51 | 6:03 | 6:51 | 3:03
08 Mon | 5:51 | 20:03 | 9:48 | 3:57 | 5:51 | 6:57 | 2:51 | 08 Thu | 5:30 | 20:30 | 9:00 | 3:31 | 5:30 | 6:31 | 2:30 | 08 Sat | 5:37 | 20:33 | 9:04 | 3:27 | 5:37 | 6:27 | 2:37 | 08 Tue | 6:04 | 20:07 | 9:57 | 3:53 | 6:04 | 6:53 | 3:04
09 Tue | 5:50 | 20:04 | 9:45 | 3:56 | 5:50 | 6:56 | 2:50 | 09 Fri | 5:29 | 20:30 | 8:59 | 3:30 | 5:29 | 6:30 | 2:29 | 09 Sun | 5:38 | 20:33 | 9:05 | 3:27 | 5:38 | 6:27 | 2:38 | 09 Wed | 6:05 | 20:06 | 9:59 | 3:54 | 6:05 | 6:54 | 3:05
10 Wed | 5:49 | 20:05 | 9:43 | 3:55 | 5:49 | 6:55 | 2:49 | 10 Sat | 5:29 | 20:31 | 8:59 | 3:29 | 5:29 | 6:29 | 2:29 | 10 Mon | 5:39 | 20:33 | 9:06 | 3:27 | 5:39 | 6:27 | 2:39 | 10 Thu | 6:06 | 20:05 | 10:01 | 3:55 | 6:06 | 6:55 | 3:06
11 Thu | 5:48 | 20:06 | 9:41 | 3:54 | 5:48 | 6:54 | 2:48 | 11 Sun | 5:29 | 20:31 | 8:58 | 3:29 | 5:29 | 6:29 | 2:29 | 11 Tue | 5:39 | 20:32 | 9:07 | 3:28 | 5:39 | 6:28 | 2:39 | 11 Fri | 6:07 | 20:04 | 10:03 | 3:56 | 6:07 | 6:56 | 3:07
12 Fri | 5:47 | 20:07 | 9:39 | 3:53 | 5:47 | 6:53 | 2:47 | 12 Mon | 5:29 | 20:32 | 8:57 | 3:28 | 5:29 | 6:28 | 2:29 | 12 Wed | 5:40 | 20:32 | 9:08 | 3:28 | 5:40 | 6:28 | 2:40 | 12 Sat | 6:08 | 20:02 | 10:06 | 3:58 | 6:08 | 6:58 | 3:08
13 Sat | 5:46 | 20:08 | 9:37 | 3:52 | 5:46 | 6:52 | 2:46 | 13 Tue | 5:29 | 20:32 | 8:57 | 3:28 | 5:29 | 6:28 | 2:29 | 13 Thu | 5:41 | 20:31 | 9:10 | 3:29 | 5:41 | 6:29 | 2:41 | 13 Sun | 6:09 | 20:01 | 10:08 | 3:59 | 6:09 | 6:59 | 3:09
14 Sun | 5:45 | 20:09 | 9:35 | 3:51 | 5:45 | 6:51 | 2:45 | 14 Wed | 5:29 | 20:32 | 8:57 | 3:28 | 5:29 | 6:28 | 2:29 | 14 Fri | 5:42 | 20:31 | 9:11 | 3:29 | 5:42 | 6:29 | 2:42 | 14 Mon | 6:10 | 20:00 | 10:10 | 4:00 | 6:10 | 7:00 | 3:10
15 Mon | 5:44 | 20:10 | 9:33 | 3:50 | 5:44 | 6:50 | 2:44 | 15 Thu | 5:29 | 20:33 | 8:56 | 3:27 | 5:29 | 6:27 | 2:29 | 15 Sat | 5:42 | 20:30 | 9:12 | 3:30 | 5:42 | 6:30 | 2:42 | 15 Tue | 6:11 | 19:58 | 10:13 | 4:02 | 6:11 | 7:02 | 3:11
16 Tue | 5:43 | 20:11 | 9:32 | 3:49 | 5:43 | 6:49 | 2:43 | 16 Fri | 5:29 | 20:33 | 8:56 | 3:27 | 5:29 | 6:27 | 2:29 | 16 Sun | 5:43 | 20:29 | 9:14 | 3:31 | 5:43 | 6:31 | 2:43 | 16 Wed | 6:12 | 19:57 | 10:15 | 4:03 | 6:12 | 7:03 | 3:12
17 Wed | 5:42 | 20:12 | 9:30 | 3:48 | 5:42 | 6:48 | 2:42 | 17 Sat | 5:29 | 20:34 | 8:56 | 3:26 | 5:29 | 6:26 | 2:29 | 17 Mon | 5:44 | 20:29 | 9:15 | 3:31 | 5:44 | 6:31 | 2:44 | 17 Thu | 6:13 | 19:55 | 10:17 | 4:05 | 6:13 | 7:05 | 3:13
18 Thu | 5:41 | 20:13 | 9:28 | 3:47 | 5:41 | 6:47 | 2:41 | 18 Sun | 5:29 | 20:34 | 8:55 | 3:26 | 5:29 | 6:26 | 2:29 | 18 Tue | 5:45 | 20:28 | 9:17 | 3:32 | 5:45 | 6:32 | 2:45 | 18 Fri | 6:14 | 19:54 | 10:20 | 4:06 | 6:14 | 7:06 | 3:14
19 Fri | 5:40 | 20:14 | 9:26 | 3:46 | 5:40 | 6:46 | 2:40 | 19 Mon | 5:29 | 20:34 | 8:55 | 3:26 | 5:29 | 6:26 | 2:29 | 19 Wed | 5:46 | 20:27 | 9:18 | 3:33 | 5:46 | 6:33 | 2:46 | 19 Sat | 6:15 | 19:53 | 10:22 | 4:07 | 6:15 | 7:07 | 3:15
20 Sat | 5:39 | 20:15 | 9:24 | 3:45 | 5:39 | 6:45 | 2:39 | 20 Tue | 5:30 | 20:34 | 8:55 | 3:26 | 5:30 | 6:26 | 2:30 | 20 Thu | 5:46 | 20:27 | 9:20 | 3:33 | 5:46 | 6:33 | 2:46 | 20 Sun | 6:16 | 19:51 | 10:25 | 4:09 | 6:16 | 7:09 | 3:16
21 Sun | 5:39 | 20:16 | 9:23 | 3:44 | 5:39 | 6:44 | 2:39 | 21 Wed | 5:30 | 20:35 | 8:55 | 3:25 | 5:30 | 6:25 | 2:30 | 21 Fri | 5:47 | 20:26 | 9:21 | 3:34 | 5:47 | 6:34 | 2:47 | 21 Mon | 6:17 | 19:50 | 10:27 | 4:10 | 6:17 | 7:10 | 3:17
22 Mon | 5:38 | 20:17 | 9:21 | 3:43 | 5:38 | 6:43 | 2:38 | 22 Thu | 5:30 | 20:35 | 8:55 | 3:25 | 5:30 | 6:25 | 2:30 | 22 Sat | 5:48 | 20:25 | 9:23 | 3:35 | 5:48 | 6:35 | 2:48 | 22 Tue | 6:18 | 19:48 | 10:30 | 4:12 | 6:18 | 7:12 | 3:18
23 Tue | 5:37 | 20:18 | 9:19 | 3:42 | 5:37 | 6:42 | 2:37 | 23 Fri | 5:30 | 20:35 | 8:55 | 3:25 | 5:30 | 6:25 | 2:30 | 23 Sun | 5:49 | 20:24 | 9:25 | 3:36 | 5:49 | 6:36 | 2:49 | 23 Wed | 6:19 | 19:47 | 10:32 | 4:13 | 6:19 | 7:13 | 3:19
24 Wed | 5:36 | 20:19 | 9:18 | 3:41 | 5:36 | 6:41 | 2:36 | 24 Sat | 5:31 | 20:35 | 8:55 | 3:25 | 5:31 | 6:25 | 2:31 | 24 Mon | 5:50 | 20:23 | 9:27 | 3:37 | 5:50 | 6:37 | 2:50 | 24 Thu | 6:20 | 19:45 | 10:34 | 4:15 | 6:20 | 7:15 | 3:20
25 Thu | 5:36 | 20:19 | 9:16 | 3:41 | 5:36 | 6:41 | 2:36 | 25 Sun | 5:31 | 20:35 | 8:56 | 3:25 | 5:31 | 6:25 | 2:31 | 25 Tue | 5:51 | 20:22 | 9:28 | 3:38 | 5:51 | 6:38 | 2:51 | 25 Fri | 6:21 | 19:44 | 10:37 | 4:16 | 6:21 | 7:16 | 3:21
26 Fri | 5:35 | 20:20 | 9:15 | 3:40 | 5:35 | 6:40 | 2:35 | 26 Mon | 5:31 | 20:35 | 8:56 | 3:25 | 5:31 | 6:25 | 2:31 | 26 Wed | 5:52 | 20:22 | 9:30 | 3:38 | 5:52 | 6:38 | 2:52 | 26 Sat | 6:22 | 19:42 | 10:39 | 4:18 | 6:22 | 7:18 | 3:22
27 Sat | 5:34 | 20:21 | 9:13 | 3:39 | 5:34 | 6:39 | 2:34 | 27 Tue | 5:32 | 20:35 | 8:56 | 3:25 | 5:32 | 6:25 | 2:32 | 27 Thu | 5:53 | 20:21 | 9:32 | 3:39 | 5:53 | 6:39 | 2:53 | 27 Sun | 6:23 | 19:41 | 10:42 | 4:19 | 6:23 | 7:19 | 3:23
28 Sun | 5:34 | 20:22 | 9:12 | 3:38 | 5:34 | 6:38 | 2:34 | 28 Wed | 5:32 | 20:35 | 8:57 | 3:25 | 5:32 | 6:25 | 2:32 | 28 Fri | 5:53 | 20:20 | 9:34 | 3:40 | 5:53 | 6:40 | 2:53 | 28 Mon | 6:23 | 19:39 | 10:45 | 4:21 | 6:23 | 7:21 | 3:23
29 Mon | 5:33 | 20:23 | 9:11 | 3:37 | 5:33 | 6:37 | 2:33 | 29 Thu | 5:32 | 20:35 | 8:57 | 3:25 | 5:32 | 6:25 | 2:32 | 29 Sat | 5:54 | 20:19 | 9:36 | 3:41 | 5:54 | 6:41 | 2:54 | 29 Tue | 6:24 | 19:37 | 10:47 | 4:23 | 6:24 | 7:23 | 3:24
30 Tue | 5:33 | 20:23 | 9:09 | 3:37 | 5:33 | 6:37 | 2:33 | 30 Fri | 5:33 | 20:35 | 8:58 | 3:25 | 5:33 | 6:25 | 2:33 | 30 Sun | 5:55 | 20:18 | 9:38 | 3:42 | 5:55 | 6:42 | 2:55 | 30 Wed | 6:25 | 19:36 | 10:50 | 4:24 | 6:25 | 7:24 | 3:25
31 Wed | 5:32 | 20:24 | 9:08 | 3:36 | 5:32 | 6:36 | 2:32 |  |  | Total | 269:07 | 104:01 | 165:06 | 194:01 | 75:06 | 31 Mon | 5:56 | 20:17 | 9:40 | 3:43 | 5:56 | 6:43 | 2:56 | 31 Thu | 6:26 | 19:34 | 10:52 | 4:26 | 6:26 | 7:26 | 3:26
|  | Total | 296:03 | 118:23 | 177:40 | 211:23 | 84:40 | [10 empty] | Total | 287:04 | 109:29 | 177:35 | 202:29 | 84:35 |  |  | Total | 318:05 | 126:00 | 192:05 | 219:00 | 99:05
2023-09-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn | 2023-10-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn | 2023-11-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn | 2023-12-01 |  |  | Dusk to dawn | Dusk to midnight | Midnight to dawn | Dusk to 3am | 3am to dawn
Date | Sunrise | Sunset | [5 empty] | Date | Sunrise | Sunset | [5 empty] | Date | Sunrise | Sunset | [5 empty] | Date | Sunrise | Sunset
01 Fri | 6:27 | 19:33 | 10:55 | 4:27 | 6:27 | 7:27 | 3:27 | 01 Sun | 6:57 | 18:43 | 12:14 | 5:17 | 6:57 | 8:17 | 3:57 | 01 Wed | 7:30 | 17:57 | 13:33 | 6:03 | 7:30 | 9:03 | 4:30 | 01 Fri | 7:05 | 16:34 | 14:30 | 7:26 | 7:05 | 10:26 | 4:05
02 Sat | 6:28 | 19:31 | 10:57 | 4:29 | 6:28 | 7:29 | 3:28 | 02 Mon | 6:58 | 18:41 | 12:17 | 5:19 | 6:58 | 8:19 | 3:58 | 02 Thu | 7:31 | 17:56 | 13:36 | 6:04 | 7:31 | 9:04 | 4:31 | 02 Sat | 7:06 | 16:34 | 14:32 | 7:26 | 7:06 | 10:26 | 4:06
03 Sun | 6:29 | 19:29 | 11:00 | 4:31 | 6:29 | 7:31 | 3:29 | 03 Tue | 6:59 | 18:39 | 12:19 | 5:21 | 6:59 | 8:21 | 3:59 | 03 Fri | 7:33 | 17:55 | 13:38 | 6:05 | 7:33 | 9:05 | 4:33 | 03 Sun | 7:07 | 16:34 | 14:33 | 7:26 | 7:07 | 10:26 | 4:07
04 Mon | 6:30 | 19:28 | 11:03 | 4:32 | 6:30 | 7:32 | 3:30 | 04 Wed | 7:00 | 18:38 | 12:22 | 5:22 | 7:00 | 8:22 | 4:00 | 04 Sat | 7:34 | 17:54 | 13:40 | 6:06 | 7:34 | 9:06 | 4:34 | 04 Mon | 7:07 | 16:33 | 14:34 | 7:27 | 7:07 | 10:27 | 4:07
05 Tue | 6:31 | 19:26 | 11:05 | 4:34 | 6:31 | 7:34 | 3:31 | 05 Thu | 7:01 | 18:36 | 12:25 | 5:24 | 7:01 | 8:24 | 4:01 | 05 Sun | 6:35 | 16:52 | 13:43 | 7:08 | 6:35 | 10:08 | 3:35 | 05 Tue | 7:08 | 16:33 | 14:35 | 7:27 | 7:08 | 10:27 | 4:08
06 Wed | 6:32 | 19:24 | 11:08 | 4:36 | 6:32 | 7:36 | 3:32 | 06 Fri | 7:02 | 18:34 | 12:27 | 5:26 | 7:02 | 8:26 | 4:02 | 06 Mon | 6:36 | 16:51 | 13:45 | 7:09 | 6:36 | 10:09 | 3:36 | 06 Wed | 7:09 | 16:33 | 14:36 | 7:27 | 7:09 | 10:27 | 4:09
07 Thu | 6:33 | 19:23 | 11:10 | 4:37 | 6:33 | 7:37 | 3:33 | 07 Sat | 7:03 | 18:33 | 12:30 | 5:27 | 7:03 | 8:27 | 4:03 | 07 Tue | 6:37 | 16:50 | 13:47 | 7:10 | 6:37 | 10:10 | 3:37 | 07 Thu | 7:10 | 16:33 | 14:37 | 7:27 | 7:10 | 10:27 | 4:10
08 Fri | 6:34 | 19:21 | 11:13 | 4:39 | 6:34 | 7:39 | 3:34 | 08 Sun | 7:04 | 18:31 | 12:33 | 5:29 | 7:04 | 8:29 | 4:04 | 08 Wed | 6:39 | 16:49 | 13:49 | 7:11 | 6:39 | 10:11 | 3:39 | 08 Fri | 7:11 | 16:33 | 14:38 | 7:27 | 7:11 | 10:27 | 4:11
09 Sat | 6:35 | 19:20 | 11:16 | 4:40 | 6:35 | 7:40 | 3:35 | 09 Mon | 7:05 | 18:30 | 12:35 | 5:30 | 7:05 | 8:30 | 4:05 | 09 Thu | 6:40 | 16:48 | 13:51 | 7:12 | 6:40 | 10:12 | 3:40 | 09 Sat | 7:12 | 16:33 | 14:39 | 7:27 | 7:12 | 10:27 | 4:12
10 Sun | 6:36 | 19:18 | 11:18 | 4:42 | 6:36 | 7:42 | 3:36 | 10 Tue | 7:06 | 18:28 | 12:38 | 5:32 | 7:06 | 8:32 | 4:06 | 10 Fri | 6:41 | 16:47 | 13:54 | 7:13 | 6:41 | 10:13 | 3:41 | 10 Sun | 7:13 | 16:33 | 14:40 | 7:27 | 7:13 | 10:27 | 4:13
11 Mon | 6:37 | 19:16 | 11:21 | 4:44 | 6:37 | 7:44 | 3:37 | 11 Wed | 7:07 | 18:27 | 12:40 | 5:33 | 7:07 | 8:33 | 4:07 | 11 Sat | 6:42 | 16:46 | 13:56 | 7:14 | 6:42 | 10:14 | 3:42 | 11 Mon | 7:14 | 16:33 | 14:40 | 7:27 | 7:14 | 10:27 | 4:14
12 Tue | 6:38 | 19:15 | 11:24 | 4:45 | 6:38 | 7:45 | 3:38 | 12 Thu | 7:08 | 18:25 | 12:43 | 5:35 | 7:08 | 8:35 | 4:08 | 12 Sun | 6:43 | 16:45 | 13:58 | 7:15 | 6:43 | 10:15 | 3:43 | 12 Tue | 7:14 | 16:34 | 14:41 | 7:26 | 7:14 | 10:26 | 4:14
13 Wed | 6:39 | 19:13 | 11:26 | 4:47 | 6:39 | 7:47 | 3:39 | 13 Fri | 7:09 | 18:23 | 12:46 | 5:37 | 7:09 | 8:37 | 4:09 | 13 Mon | 6:44 | 16:44 | 14:00 | 7:16 | 6:44 | 10:16 | 3:44 | 13 Wed | 7:15 | 16:34 | 14:42 | 7:26 | 7:15 | 10:26 | 4:15
14 Thu | 6:40 | 19:11 | 11:29 | 4:49 | 6:40 | 7:49 | 3:40 | 14 Sat | 7:10 | 18:22 | 12:48 | 5:38 | 7:10 | 8:38 | 4:10 | 14 Tue | 6:46 | 16:44 | 14:02 | 7:16 | 6:46 | 10:16 | 3:46 | 14 Thu | 7:16 | 16:34 | 14:42 | 7:26 | 7:16 | 10:26 | 4:16
15 Fri | 6:41 | 19:09 | 11:31 | 4:51 | 6:41 | 7:51 | 3:41 | 15 Sun | 7:11 | 18:20 | 12:51 | 5:40 | 7:11 | 8:40 | 4:11 | 15 Wed | 6:47 | 16:43 | 14:04 | 7:17 | 6:47 | 10:17 | 3:47 | 15 Fri | 7:17 | 16:34 | 14:43 | 7:26 | 7:17 | 10:26 | 4:17
16 Sat | 6:42 | 19:08 | 11:34 | 4:52 | 6:42 | 7:52 | 3:42 | 16 Mon | 7:12 | 18:19 | 12:53 | 5:41 | 7:12 | 8:41 | 4:12 | 16 Thu | 6:48 | 16:42 | 14:06 | 7:18 | 6:48 | 10:18 | 3:48 | 16 Sat | 7:17 | 16:34 | 14:43 | 7:26 | 7:17 | 10:26 | 4:17
17 Sun | 6:43 | 19:06 | 11:37 | 4:54 | 6:43 | 7:54 | 3:43 | 17 Tue | 7:13 | 18:17 | 12:56 | 5:43 | 7:13 | 8:43 | 4:13 | 17 Fri | 6:49 | 16:41 | 14:08 | 7:19 | 6:49 | 10:19 | 3:49 | 17 Sun | 7:18 | 16:35 | 14:43 | 7:25 | 7:18 | 10:25 | 4:18
18 Mon | 6:44 | 19:04 | 11:39 | 4:56 | 6:44 | 7:56 | 3:44 | 18 Wed | 7:15 | 18:16 | 12:59 | 5:44 | 7:15 | 8:44 | 4:15 | 18 Sat | 6:50 | 16:40 | 14:10 | 7:20 | 6:50 | 10:20 | 3:50 | 18 Mon | 7:19 | 16:35 | 14:44 | 7:25 | 7:19 | 10:25 | 4:19
19 Tue | 6:45 | 19:03 | 11:42 | 4:57 | 6:45 | 7:57 | 3:45 | 19 Thu | 7:16 | 18:14 | 13:01 | 5:46 | 7:16 | 8:46 | 4:16 | 19 Sun | 6:51 | 16:40 | 14:12 | 7:20 | 6:51 | 10:20 | 3:51 | 19 Tue | 7:19 | 16:36 | 14:44 | 7:24 | 7:19 | 10:24 | 4:19
20 Wed | 6:46 | 19:01 | 11:45 | 4:59 | 6:46 | 7:59 | 3:46 | 20 Fri | 7:17 | 18:13 | 13:04 | 5:47 | 7:17 | 8:47 | 4:17 | 20 Mon | 6:53 | 16:39 | 14:13 | 7:21 | 6:53 | 10:21 | 3:53 | 20 Wed | 7:20 | 16:36 | 14:44 | 7:24 | 7:20 | 10:24 | 4:20
21 Thu | 6:47 | 18:59 | 11:47 | 5:01 | 6:47 | 8:01 | 3:47 | 21 Sat | 7:18 | 18:12 | 13:06 | 5:48 | 7:18 | 8:48 | 4:18 | 21 Tue | 6:54 | 16:38 | 14:15 | 7:22 | 6:54 | 10:22 | 3:54 | 21 Thu | 7:20 | 16:36 | 14:44 | 7:24 | 7:20 | 10:24 | 4:20
22 Fri | 6:48 | 18:58 | 11:50 | 5:02 | 6:48 | 8:02 | 3:48 | 22 Sun | 7:19 | 18:10 | 13:09 | 5:50 | 7:19 | 8:50 | 4:19 | 22 Wed | 6:55 | 16:38 | 14:17 | 7:22 | 6:55 | 10:22 | 3:55 | 22 Fri | 7:21 | 16:37 | 14:44 | 7:23 | 7:21 | 10:23 | 4:21
23 Sat | 6:49 | 18:56 | 11:53 | 5:04 | 6:49 | 8:04 | 3:49 | 23 Mon | 7:20 | 18:09 | 13:11 | 5:51 | 7:20 | 8:51 | 4:20 | 23 Thu | 6:56 | 16:37 | 14:19 | 7:23 | 6:56 | 10:23 | 3:56 | 23 Sat | 7:21 | 16:38 | 14:44 | 7:22 | 7:21 | 10:22 | 4:21
24 Sun | 6:50 | 18:54 | 11:55 | 5:06 | 6:50 | 8:06 | 3:50 | 24 Tue | 7:21 | 18:07 | 13:14 | 5:53 | 7:21 | 8:53 | 4:21 | 24 Fri | 6:57 | 16:37 | 14:20 | 7:23 | 6:57 | 10:23 | 3:57 | 24 Sun | 7:22 | 16:38 | 14:44 | 7:22 | 7:22 | 10:22 | 4:22
25 Mon | 6:51 | 18:53 | 11:58 | 5:07 | 6:51 | 8:07 | 3:51 | 25 Wed | 7:22 | 18:06 | 13:16 | 5:54 | 7:22 | 8:54 | 4:22 | 25 Sat | 6:58 | 16:36 | 14:22 | 7:24 | 6:58 | 10:24 | 3:58 | 25 Mon | 7:22 | 16:39 | 14:43 | 7:21 | 7:22 | 10:21 | 4:22
26 Tue | 6:52 | 18:51 | 12:01 | 5:09 | 6:52 | 8:09 | 3:52 | 26 Thu | 7:23 | 18:05 | 13:19 | 5:55 | 7:23 | 8:55 | 4:23 | 26 Sun | 6:59 | 16:36 | 14:23 | 7:24 | 6:59 | 10:24 | 3:59 | 26 Tue | 7:23 | 16:39 | 14:43 | 7:21 | 7:23 | 10:21 | 4:23
27 Wed | 6:53 | 18:49 | 12:03 | 5:11 | 6:53 | 8:11 | 3:53 | 27 Fri | 7:25 | 18:03 | 13:21 | 5:57 | 7:25 | 8:57 | 4:25 | 27 Mon | 7:00 | 16:35 | 14:25 | 7:25 | 7:00 | 10:25 | 4:00 | 27 Wed | 7:23 | 16:40 | 14:43 | 7:20 | 7:23 | 10:20 | 4:23
28 Thu | 6:54 | 18:48 | 12:06 | 5:12 | 6:54 | 8:12 | 3:54 | 28 Sat | 7:26 | 18:02 | 13:24 | 5:58 | 7:26 | 8:58 | 4:26 | 28 Tue | 7:01 | 16:35 | 14:26 | 7:25 | 7:01 | 10:25 | 4:01 | 28 Thu | 7:23 | 16:41 | 14:42 | 7:19 | 7:23 | 10:19 | 4:23
29 Fri | 6:55 | 18:46 | 12:09 | 5:14 | 6:55 | 8:14 | 3:55 | 29 Sun | 7:27 | 18:01 | 13:26 | 5:59 | 7:27 | 8:59 | 4:27 | 29 Wed | 7:02 | 16:35 | 14:28 | 7:25 | 7:02 | 10:25 | 4:02 | 29 Fri | 7:23 | 16:41 | 14:42 | 7:19 | 7:23 | 10:19 | 4:23
30 Sat | 6:56 | 18:44 | 12:11 | 5:16 | 6:56 | 8:16 | 3:56 | 30 Mon | 7:28 | 17:59 | 13:29 | 6:01 | 7:28 | 9:01 | 4:28 | 30 Thu | 7:03 | 16:34 | 14:29 | 7:26 | 7:03 | 10:26 | 4:03 | 30 Sat | 7:24 | 16:42 | 14:41 | 7:18 | 7:24 | 10:18 | 4:24
|  | Total | 346:27 | 145:43 | 200:44 | 235:43 | 110:44 | 31 Tue | 7:29 | 17:58 | 13:31 | 6:02 | 7:29 | 9:02 | 4:29 |  |  | Total | 421:49 | 214:14 | 207:35 | 304:14 | 117:35 | 31 Sun | 7:24 | 16:43 | 14:41 | 7:17 | 7:24 | 10:17 | 4:24
[10 empty] | Total | 399:27 | 175:58 | 223:29 | 268:58 | 130:29 | [10 empty] | Total | 454:51 | 229:27 | 225:24 | 322:27 | 132:24

## OpHrs_Summary (Ref)
ANNUAL operating hours - Summary
SunEarthTools.com
coordinates: 40.5853804, -105.0847024
location: 40.76000000,-73.98400000
|  | Time (hr:mm) |  |  |  |  | Time (fractional hours)
| Month | Dusk to dawn | Dusk to mignight | Midnight to dawn | Dusk to 3am | 3am to dawn | Dusk to dawn | Dusk to mignight | Midnight to dawn | Dusk to 3am | 3am to dawn
| January | 1900-01-17 12:36 | 1900-01-08 01:14 | 1900-01-08 11:23 | 1900-01-11 22:14 | 1900-01-04 14:23 | 444.6047 | 217.2269 | 227.3778 | 310.2269 | 134.3778
| February | 1900-01-14 13:09 | 1900-01-06 11:53 | 1900-01-07 01:17 | 1900-01-09 23:53 | 1900-01-03 13:17 | 373.1553 | 179.8786 | 193.2767 | 263.8786 | 109.2767
| March | 1900-01-14 13:13 | 1900-01-05 17:53 | 1900-01-07 19:21 | 1900-01-09 14:53 | 1900-01-03 22:21 | 373.2236 | 161.8767 | 211.3469 | 254.8767 | 118.3469
| April | 1900-01-12 08:47 | 1900-01-04 09:59 | 1900-01-06 22:49 | 1900-01-08 03:59 | 1900-01-03 04:49 | 320.7911 | 129.9761 | 190.815 | 219.9761 | 100.815
| May | 1900-01-11 08:03 | 1900-01-03 22:23 | 1900-01-06 09:40 | 1900-01-07 19:23 | 1900-01-02 12:40 | 296.0558 | 118.3839 | 177.6719 | 211.3839 | 84.6719
| June | 1900-01-10 05:07 | 1900-01-03 08:01 | 1900-01-05 21:06 | 1900-01-07 02:01 | 1900-01-02 03:06 | 269.1181 | 104.0136 | 165.1044 | 194.0136 | 75.1044
| July | 1900-01-10 23:04 | 1900-01-03 13:29 | 1900-01-06 09:35 | 1900-01-07 10:29 | 1900-01-02 12:35 | 287.0667 | 109.4786 | 177.5881 | 202.4786 | 84.5881
| August | 1900-01-12 06:05 | 1900-01-04 06:00 | 1900-01-07 00:05 | 1900-01-08 03:00 | 1900-01-03 03:05 | 318.0844 | 125.9942 | 192.0903 | 218.9942 | 99.0903
| September | 1900-01-13 10:27 | 1900-01-05 01:43 | 1900-01-07 08:44 | 1900-01-08 19:43 | 1900-01-03 14:44 | 346.4439 | 145.7133 | 200.7306 | 235.7133 | 110.7306
| October | 1900-01-15 15:27 | 1900-01-06 07:58 | 1900-01-08 07:29 | 1900-01-10 04:58 | 1900-01-04 10:29 | 399.4531 | 175.9628 | 223.4903 | 268.9628 | 130.4903
| November | 1900-01-16 13:49 | 1900-01-07 22:14 | 1900-01-07 15:35 | 1900-01-11 16:14 | 1900-01-03 21:35 | 421.8214 | 214.2361 | 207.5853 | 304.2361 | 117.5853
| December | 1900-01-17 22:51 | 1900-01-08 13:27 | 1900-01-08 09:24 | 1900-01-12 10:27 | 1900-01-04 12:24 | 454.8461 | 229.4483 | 225.3978 | 322.4483 | 132.3978
| Total Winter: | 1900-05-07 11:57 | 1900-02-27 10:59 | 1900-03-09 00:58 | 1900-03-29 19:59 | 1900-02-06 15:58 | 3083.9511 | 1426.9894 | 1656.9617 | 2155.9894 | 927.9617
| Total Summer: | 1900-02-18 20:43 | 1900-01-19 05:12 | 1900-01-29 15:31 | 1900-02-03 11:12 | 1900-01-14 09:31 | 1220.7131 | 485.1997 | 735.5133 | 851.1997 | 369.5133
| Total Year: | 1900-06-27 08:40 | 1900-03-19 16:11 | 1900-04-08 16:28 | 1900-05-04 07:11 | 1900-02-22 01:28 | 4304.6642 | 1912.1892 | 2392.475 | 3007.1892 | 1297.475
Hours
| Time Range | Summer | Winter
| Dusk - Midnight | 485.1997 | 1426.9894
| Midnight - 3 am | 366 | 729
| 3 am - Dawn | 369.5133 | 927.9617
| Total: | 4304.6642 | <------ Total hours from dusk to dawn